## Read Me
Alex West WWTP - estimate bill of quantities
Prepared 22 Oct 2026 by Claude for Mohamed. Quantity estimate from the available model and workbooks; not a priced or tender BOQ.
Sources
1. 3D coordination model Alex-West-Combined-Coordination.blend (19 Oct 2026): 15,195 closed meshes for 23 structure types (34 structures incl. typical copies); element volumes, face areas, levels, pile stubs.
2. Pipe execution packages v3 (21 Oct 2026): 45 lines, lengths, sizes, fittings, crossings.
3. Pipe sequence and methodology workbook (22 Oct 2026): GWL -1.50, sheet piles, dewatering, piled slabs, flotation.
Method
Every model element is classified by its name and category into a BOQ class (blinding, RC base / wall / slab / column-beam / misc / plinth, mass fill, steel, grating, handrails, stairs, piles, equipment, water). Water surfaces are excluded.
Concrete = closed-solid volume. Formwork = vertical faces + soffits of elevated slabs/beams/secondary elements. Reinforcement = volume x ratio. Excavation = offset prism from footprint below NG.
Sheets
Summary - totals per bill and key quantities; BOQ - priced bill (enter rates); Inputs - assumptions; Take-off - model data per structure and class; Structures - footprints, excavation, backfill, piles; Pipes - per-line pipe quantities; Exclusions - what is not covered.
Confidence
B = structural model or detailed design source (aeration Rev02, FST DD-004, pipe lines). C = civil-guide or provisional envelope. D = tender envelope, placeholder or allowance.
Colour key
Blue = source data; black = formula; yellow = enter / edit.

## Summary
Alex West WWTP - estimate BOQ summary
Amounts fill in as rates are entered on the BOQ sheet. Key quantities are totals of the BOQ by code.
Bill | Description | Amount | Share
01 | Grit removal and fine screens | 0 | 0%
02 | Primary sedimentation tanks (8 basins) | 0 | 0%
03 | Intermediate pumping station incl. shared IPS/RAS motor hall | 0 | 0%
04 | Aeration tanks | 0 | 0%
05 | Secondary distribution chambers A-C (3 nr) | 0 | 0%
06 | Final sedimentation tanks A-L (12 nr) | 0 | 0%
07 | RAS/WAS pumping station | 0 | 0%
08 | Chlorine contact tank | 0 | 0%
09 | Fire / service / cooling water structure | 0 | 0%
10 | Air blower building | 0 | 0%
11 | Primary sludge thickeners A-D (4 nr) | 0 | 0%
12 | Anaerobic digesters 01-08 (8 nr) | 0 | 0%
13 | Gas holder plinths 01-04 (4 nr) | 0 | 0%
14 | Gas holder blower house | 0 | 0%
15 | Digested sludge buildings 01-02 (2 nr) | 0 | 0%
16 | Grease pump station | 0 | 0%
17 | Scum pump station | 0 | 0%
18 | WAS pre-dewatering building | 0 | 0%
19 | THP system platform | 0 | 0%
20 | Final dewatering building | 0 | 0%
21 | CHP building | 0 | 0%
22 | Chlorination storage building | 0 | 0%
23 | Air blowers power house | 0 | 0%
24 | Underground pipework - 45 printed lines, 201 packages (DLU-002 Rev 03) | 0 | 0%
25 | Site-wide and provisional items | 0 | 0%
| Total (excluding preliminaries, M&E, contingency) | 0
Key quantities
Code | Quantity | Unit | Description
RC_BASE | 88694.9491 | m3 | RC rafts, bases, floors, foundations (incl. pipe slabs)
RC_WALL | 41276.1457 | m3 | RC walls
RC_SLAB | 5605.6017 | m3 | RC suspended slabs / decks / roofs
RC_COLBEAM | 432.1123 | m3 | RC columns / beams
RC_MISC | 7944.6378 | m3 | RC channels, baffles, weirs, chambers
RC_PLINTH | 1816.2575 | m3 | RC plinths
RC_BRIDGE | 21.3214 | m3 | RC thickener bridges
BLINDING | 6091.6547 | m3 | Blinding
MASS_FILL | 590.7426 | m3 | Mass concrete fill
FORMWORK | 221442.0852 | m2 | Formwork
REBAR | 17293.2066 | t | Reinforcement
STEEL | 0 | t | Structural steel
PILE | 15994 | no. | Piles 600 mm (model + allowances + pipe placeholder)
EXC | 511247.1023 | m3 | Excavation
BACKFILL | 184618.4453 | m3 | Backfill
SHEET | 116308.6076 | m2 | Temporary sheet piles
PIPE | 8294.3302 | m | Pipes
FITTING | 474 | no. | Pipe fittings
HANDRAIL | 5411.8366 | m | Handrails
SITEFILL | 378367.47 | m3 | Site raising (provisional)
All RC | 145791.0255 | m3 | All reinforced concrete
Cross-checks
Aeration raft: model vs aeration estimate |  | 30119.834 | 30012.624 | Model RC_BASE for aeration vs 30,012.6 m3 net raft (AW-AER Tracking Documentation, 18 Oct 2026)
Aeration piles in model vs tracking |  | 3672 | 3672 | 3,672 model piles; 2,079 recorded done, 19 defect, 1,568 pending (17 Oct 2026) - BOQ is gross

## BOQ
Alex West WWTP - estimate bill of quantities (whole project, from available information)
Quantities are formulas on the Take-off, Structures and Pipes sheets. Enter rates in the yellow column (currency on Inputs). Confidence: B = structural / detailed model; C = civil-guide or provisional envelope; D = tender envelope, placeholder or allowance.
Bill | Item | Description | Unit | Quantity | Rate | Amount | Code | Basis / source | Confidence
01 |  | Grit removal and fine screens
01 | 01.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 1180.792 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
01 | 01.02 | Backfill around structure to NG in compacted layers | m3 | 1002.792 |  | 0 | BACKFILL | Structures sheet | C
01 | 01.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 65 |  | 0 | PILE | Footprint x PILE_DENS | D
01 | 01.04 | Mass concrete fill / benching to sloped floors | m3 | 273.4294 |  | 0 | MASS_FILL | Model volume | C
01 | 01.05 | Reinforced concrete rafts, bases, floors and foundations | m3 | 489.2294 |  | 0 | RC_BASE | Model volume | C
01 | 01.06 | Reinforced concrete walls and parapets | m3 | 967.4698 |  | 0 | RC_WALL | Model volume | C
01 | 01.07 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 224.8037 |  | 0 | RC_SLAB | Model volume | C
01 | 01.08 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 31.329 |  | 0 | RC_MISC | Model volume | C
01 | 01.09 | Formwork to vertical faces and soffits of elevated elements | m2 | 4909.4595 |  | 0 | FORMWORK | Model face areas | C
01 | 01.10 | High-yield steel reinforcement | t | 221.0906 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
01 | 01.11 | Handrails (run length) | m | 119.3 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
01 | 01.12 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 41.3814 |  | 0 | STAIRS | Model volume; 38 modelled elements | D
02 |  | Primary sedimentation tanks (8 basins)
02 | 02.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 56094.7609 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
02 | 02.02 | Backfill around structure to NG in compacted layers | m3 | 14347.6909 |  | 0 | BACKFILL | Structures sheet | C
02 | 02.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 646 |  | 0 | PILE | Footprint x PILE_DENS | D
02 | 02.04 | Plain concrete blinding / screed | m3 | 1104.2745 |  | 0 | BLINDING | Model volume | C
02 | 02.05 | Mass concrete fill / benching to sloped floors | m3 | 317.3132 |  | 0 | MASS_FILL | Model volume | C
02 | 02.06 | Reinforced concrete rafts, bases, floors and foundations | m3 | 6012.3696 |  | 0 | RC_BASE | Model volume | C
02 | 02.07 | Reinforced concrete walls and parapets | m3 | 2144.7301 |  | 0 | RC_WALL | Model volume | C
02 | 02.08 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 267.2185 |  | 0 | RC_SLAB | Model volume | C
02 | 02.09 | Reinforced concrete columns, beams and piers | m3 | 47.6065 |  | 0 | RC_COLBEAM | Model volume | C
02 | 02.10 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 356.3057 |  | 0 | RC_MISC | Model volume | C
02 | 02.11 | Formwork to vertical faces and soffits of elevated elements | m2 | 15309.2697 |  | 0 | FORMWORK | Model face areas | C
02 | 02.12 | High-yield steel reinforcement | t | 1033.2131 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
02 | 02.13 | Handrails (run length) | m | 1121.6 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
02 | 02.14 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 64.0469 |  | 0 | STAIRS | Model volume; 90 modelled elements | D
03 |  | Intermediate pumping station incl. shared IPS/RAS motor hall
03 | 03.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 11780.0457 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
03 | 03.02 | Backfill around structure to NG in compacted layers | m3 | 5966.7957 |  | 0 | BACKFILL | Structures sheet | C
03 | 03.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 118 |  | 0 | PILE | Footprint x PILE_DENS | D
03 | 03.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 776.2829 |  | 0 | RC_BASE | Model volume | C
03 | 03.05 | Reinforced concrete walls and parapets | m3 | 1428.0989 |  | 0 | RC_WALL | Model volume | C
03 | 03.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 371.4004 |  | 0 | RC_SLAB | Model volume | C
03 | 03.07 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 223.0756 |  | 0 | RC_MISC | Model volume | C
03 | 03.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 6403.9658 |  | 0 | FORMWORK | Model face areas | C
03 | 03.09 | High-yield steel reinforcement | t | 360.278 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
03 | 03.10 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 47.0063 |  | 0 | STAIRS | Model volume; 330 modelled elements | D
04 |  | Aeration tanks
04 | 04.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 89258.0712 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | B
04 | 04.02 | Backfill around structure to NG in compacted layers | m3 | 5270.5512 |  | 0 | BACKFILL | Structures sheet | B
04 | 04.03 | Piles 600 mm diameter (CFA / bored) - length to pile design | no. | 3672 |  | 0 | PILE | Model pile count | B
04 | 04.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 30119.834 |  | 0 | RC_BASE | Model volume | B
04 | 04.05 | Reinforced concrete walls and parapets | m3 | 12805.6583 |  | 0 | RC_WALL | Model volume | B
04 | 04.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 764.2811 |  | 0 | RC_SLAB | Model volume | B
04 | 04.07 | Reinforced concrete columns, beams and piers | m3 | 209.0851 |  | 0 | RC_COLBEAM | Model volume | B
04 | 04.08 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 5183.7867 |  | 0 | RC_MISC | Model volume | B
04 | 04.09 | Formwork to vertical faces and soffits of elevated elements | m2 | 64487.6724 |  | 0 | FORMWORK | Model face areas | B
04 | 04.10 | High-yield steel reinforcement | t | 5826.4985 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | C
04 | 04.11 | Handrails (run length) | m | 3080.1001 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
04 | 04.12 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 8.6025 |  | 0 | STAIRS | Model volume; 15 modelled elements | D
05 |  | Secondary distribution chambers A-C (3 nr)
05 | 05.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 5222.751 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
05 | 05.02 | Backfill around structure to NG in compacted layers | m3 | 3770.751 |  | 0 | BACKFILL | Structures sheet | C
05 | 05.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 69 |  | 0 | PILE | Footprint x PILE_DENS | D
05 | 05.04 | Plain concrete blinding / screed | m3 | 222.2762 |  | 0 | BLINDING | Model volume | C
05 | 05.05 | Reinforced concrete rafts, bases, floors and foundations | m3 | 414.0695 |  | 0 | RC_BASE | Model volume | C
05 | 05.06 | Reinforced concrete walls and parapets | m3 | 351.8283 |  | 0 | RC_WALL | Model volume | C
05 | 05.07 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 64.7489 |  | 0 | RC_SLAB | Model volume | C
05 | 05.08 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 374.271 |  | 0 | RC_MISC | Model volume | C
05 | 05.09 | Formwork to vertical faces and soffits of elevated elements | m2 | 4308.4857 |  | 0 | FORMWORK | Model face areas | C
05 | 05.10 | High-yield steel reinforcement | t | 150.634 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
05 | 05.11 | Handrails (run length) | m | 255.8877 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
05 | 05.12 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 10.6617 |  | 0 | STAIRS | Model volume; 6 modelled elements | D
06 |  | Final sedimentation tanks A-L (12 nr)
06 | 06.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 150229.8286 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | B
06 | 06.02 | Backfill around structure to NG in compacted layers | m3 | 33936.5286 |  | 0 | BACKFILL | Structures sheet | B
06 | 06.03 | Piles 600 mm diameter (CFA / bored) - length to pile design | no. | 2556 |  | 0 | PILE | Model pile count (FST stubs are placeholders) | B
06 | 06.04 | Plain concrete blinding / screed | m3 | 3233.5091 |  | 0 | BLINDING | Model volume | B
06 | 06.05 | Reinforced concrete rafts, bases, floors and foundations | m3 | 22338.2022 |  | 0 | RC_BASE | Model volume | B
06 | 06.06 | Reinforced concrete walls and parapets | m3 | 8105.8006 |  | 0 | RC_WALL | Model volume | B
06 | 06.07 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 1060.1937 |  | 0 | RC_SLAB | Model volume | B
06 | 06.08 | Reinforced concrete columns, beams and piers | m3 | 38.8969 |  | 0 | RC_COLBEAM | Model volume | B
06 | 06.09 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 1098.4054 |  | 0 | RC_MISC | Model volume | B
06 | 06.10 | Formwork to vertical faces and soffits of elevated elements | m2 | 42490.4087 |  | 0 | FORMWORK | Model face areas | B
06 | 06.11 | High-yield steel reinforcement | t | 3812.619 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | C
06 | 06.12 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 49.8997 |  | 0 | STAIRS | Model volume; 348 modelled elements | D
07 |  | RAS/WAS pumping station
07 | 07.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 6607.7558 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
07 | 07.02 | Backfill around structure to NG in compacted layers | m3 | 5254.0258 |  | 0 | BACKFILL | Structures sheet | C
07 | 07.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 53 |  | 0 | PILE | Footprint x PILE_DENS | D
07 | 07.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 404.6505 |  | 0 | RC_BASE | Model volume | C
07 | 07.05 | Reinforced concrete walls and parapets | m3 | 969.1038 |  | 0 | RC_WALL | Model volume | C
07 | 07.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 65.2814 |  | 0 | RC_SLAB | Model volume | C
07 | 07.07 | Formwork to vertical faces and soffits of elevated elements | m2 | 3458.9502 |  | 0 | FORMWORK | Model face areas | C
07 | 07.08 | High-yield steel reinforcement | t | 187.4587 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
08 |  | Chlorine contact tank
08 | 08.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 31602.2958 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
08 | 08.02 | Backfill around structure to NG in compacted layers | m3 | 9113.2658 |  | 0 | BACKFILL | Structures sheet | C
08 | 08.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 677 |  | 0 | PILE | Footprint x PILE_DENS | D
08 | 08.04 | Plain concrete blinding / screed | m3 | 720.69 |  | 0 | BLINDING | Model volume | C
08 | 08.05 | Reinforced concrete rafts, bases, floors and foundations | m3 | 2676.7586 |  | 0 | RC_BASE | Model volume | C
08 | 08.06 | Reinforced concrete walls and parapets | m3 | 1000.6885 |  | 0 | RC_WALL | Model volume | C
08 | 08.07 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 40.56 |  | 0 | RC_SLAB | Model volume | C
08 | 08.08 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 349.2759 |  | 0 | RC_MISC | Model volume | C
08 | 08.09 | Formwork to vertical faces and soffits of elevated elements | m2 | 8196.936 |  | 0 | FORMWORK | Model face areas | C
08 | 08.10 | High-yield steel reinforcement | t | 477.1882 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
08 | 08.11 | Handrails (run length) | m | 234.714 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
08 | 08.12 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 3.5794 |  | 0 | STAIRS | Model volume; 127 modelled elements | D
09 |  | Fire / service / cooling water structure
09 | 09.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 7851.0588 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
09 | 09.02 | Backfill around structure to NG in compacted layers | m3 | 3854.2788 |  | 0 | BACKFILL | Structures sheet | C
09 | 09.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 74 |  | 0 | PILE | Footprint x PILE_DENS | D
09 | 09.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 352.832 |  | 0 | RC_BASE | Model volume | C
09 | 09.05 | Reinforced concrete walls and parapets | m3 | 902.2027 |  | 0 | RC_WALL | Model volume | C
09 | 09.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 233.07 |  | 0 | RC_SLAB | Model volume | C
09 | 09.07 | Reinforced concrete columns, beams and piers | m3 | 35.7199 |  | 0 | RC_COLBEAM | Model volume | C
09 | 09.08 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 24.855 |  | 0 | RC_MISC | Model volume | C
09 | 09.09 | Reinforced concrete equipment plinths and pads | m3 | 5.2875 |  | 0 | RC_PLINTH | Model volume | C
09 | 09.10 | Formwork to vertical faces and soffits of elevated elements | m2 | 6166.2297 |  | 0 | FORMWORK | Model face areas | C
09 | 09.11 | High-yield steel reinforcement | t | 204.4442 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
09 | 09.12 | Handrails (run length) | m | 104.9555 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
09 | 09.13 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 7.791 |  | 0 | STAIRS | Model volume; 9 modelled elements | D
09 | 09.14 | Equipment envelopes in model (blowers, cranes) - M&E supply, count for reference | no. | 28 | excluded | 0 | EQUIP | Model element count | C
09 | 09.15 | Doors and glazing envelopes in model - architectural, count for reference | no. | 18 | excluded | 0 | ARCH | Model element count | C
10 |  | Air blower building
10 | 10.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 0 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
10 | 10.02 | Backfill around structure to NG in compacted layers | m3 | 0 |  | 0 | BACKFILL | Structures sheet | C
10 | 10.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 42 |  | 0 | PILE | Footprint x PILE_DENS | D
10 | 10.04 | Plain concrete blinding / screed | m3 | 34.7361 |  | 0 | BLINDING | Model volume | C
10 | 10.05 | Reinforced concrete rafts, bases, floors and foundations | m3 | 135.3761 |  | 0 | RC_BASE | Model volume | C
10 | 10.06 | Reinforced concrete walls and parapets | m3 | 259.8236 |  | 0 | RC_WALL | Model volume | C
10 | 10.07 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 96.8767 |  | 0 | RC_SLAB | Model volume | C
10 | 10.08 | Reinforced concrete columns, beams and piers | m3 | 73.2998 |  | 0 | RC_COLBEAM | Model volume | C
10 | 10.09 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 63.3102 |  | 0 | RC_MISC | Model volume | C
10 | 10.10 | Reinforced concrete equipment plinths and pads | m3 | 15 |  | 0 | RC_PLINTH | Model volume | C
10 | 10.11 | Formwork to vertical faces and soffits of elevated elements | m2 | 3506.9725 |  | 0 | FORMWORK | Model face areas | C
10 | 10.12 | High-yield steel reinforcement | t | 86.0788 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
10 | 10.13 | Equipment envelopes in model (blowers, cranes) - M&E supply, count for reference | no. | 24 | excluded | 0 | EQUIP | Model element count | C
10 | 10.14 | Doors and glazing envelopes in model - architectural, count for reference | no. | 2 | excluded | 0 | ARCH | Model element count | C
11 |  | Primary sludge thickeners A-D (4 nr)
11 | 11.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 1649.2796 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | C
11 | 11.02 | Backfill around structure to NG in compacted layers | m3 | 335.8116 |  | 0 | BACKFILL | Structures sheet | C
11 | 11.03 | Piles 600 mm diameter (CFA / bored) - length to pile design | no. | 164 |  | 0 | PILE | Model pile count | C
11 | 11.04 | Plain concrete blinding / screed | m3 | 392.6289 |  | 0 | BLINDING | Model volume | C
11 | 11.05 | Reinforced concrete rafts, bases, floors and foundations | m3 | 1230.4679 |  | 0 | RC_BASE | Model volume | C
11 | 11.06 | Reinforced concrete walls and parapets | m3 | 819.4337 |  | 0 | RC_WALL | Model volume | C
11 | 11.07 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 6.6 |  | 0 | RC_SLAB | Model volume | C
11 | 11.08 | Reinforced concrete columns, beams and piers | m3 | 27.5041 |  | 0 | RC_COLBEAM | Model volume | C
11 | 11.09 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 146.5103 |  | 0 | RC_MISC | Model volume | C
11 | 11.10 | Reinforced concrete bridge carrying the thickener mechanism (beams, verticals, diagonals, bracing as modelled) | m3 | 21.3214 |  | 0 | RC_BRIDGE | Model volume | C
11 | 11.11 | Formwork to vertical faces and soffits of elevated elements | m2 | 4923.2155 |  | 0 | FORMWORK | Model face areas | C
11 | 11.12 | High-yield steel reinforcement | t | 275.5002 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
11 | 11.13 | 6 mm steel chequer-plate deck on thickener bridge | m2 | 141.4799 |  | 0 | GRATING | Model top area | C
11 | 11.14 | Handrails (run length) | m | 71.4479 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
11 | 11.15 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 22.7936 |  | 0 | STAIRS | Model volume; 32 modelled elements | D
12 |  | Anaerobic digesters 01-08 (8 nr)
12 | 12.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 7410.5415 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
12 | 12.02 | Backfill around structure to NG in compacted layers | m3 | 1559.4215 |  | 0 | BACKFILL | Structures sheet | D
12 | 12.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 1064 |  | 0 | PILE | Footprint x PILE_DENS | D
12 | 12.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 9975.3195 |  | 0 | RC_BASE | Model volume | D
12 | 12.05 | Reinforced concrete walls and parapets | m3 | 9645.7374 |  | 0 | RC_WALL | Model volume | D
12 | 12.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 1208.5357 |  | 0 | RC_SLAB | Model volume | D
12 | 12.07 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 35.4369 |  | 0 | RC_MISC | Model volume | D
12 | 12.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 36625.9392 |  | 0 | FORMWORK | Model face areas | D
12 | 12.09 | High-yield steel reinforcement | t | 2579.4789 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
12 | 12.10 | Handrails (run length) | m | 423.8315 |  | 0 | HANDRAIL | Model rail members / RAILS_PER_RUN; indicative in model | D
12 | 12.11 | Stairs, treads, landings and access steps (material to design) - modelled volume | m3 | 12.8628 |  | 0 | STAIRS | Model volume; 8 modelled elements | D
13 |  | Gas holder plinths 01-04 (4 nr)
13 | 13.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 1860.6703 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
13 | 13.02 | Backfill around structure to NG in compacted layers | m3 | 412.9903 |  | 0 | BACKFILL | Structures sheet | D
13 | 13.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 184 |  | 0 | PILE | Footprint x PILE_DENS | D
13 | 13.04 | Reinforced concrete equipment plinths and pads | m3 | 904.756 |  | 0 | RC_PLINTH | Model volume | D
13 | 13.05 | Formwork to vertical faces and soffits of elevated elements | m2 | 150.7955 |  | 0 | FORMWORK | Model face areas | D
13 | 13.06 | High-yield steel reinforcement | t | 72.3805 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
14 |  | Gas holder blower house
14 | 14.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 95.3916 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
14 | 14.02 | Backfill around structure to NG in compacted layers | m3 | 47.9516 |  | 0 | BACKFILL | Structures sheet | D
14 | 14.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 7 |  | 0 | PILE | Footprint x PILE_DENS | D
14 | 14.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 17.784 |  | 0 | RC_BASE | Model volume | D
14 | 14.05 | Reinforced concrete walls and parapets | m3 | 60.5261 |  | 0 | RC_WALL | Model volume | D
14 | 14.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 13.52 |  | 0 | RC_SLAB | Model volume | D
14 | 14.07 | Reinforced concrete equipment plinths and pads | m3 | 1.44 |  | 0 | RC_PLINTH | Model volume | D
14 | 14.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 527.7685 |  | 0 | FORMWORK | Model face areas | D
14 | 14.09 | High-yield steel reinforcement | t | 12.2493 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
15 |  | Digested sludge buildings 01-02 (2 nr)
15 | 15.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 1856.2041 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
15 | 15.02 | Backfill around structure to NG in compacted layers | m3 | 522.2741 |  | 0 | BACKFILL | Structures sheet | D
15 | 15.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 122 |  | 0 | PILE | Footprint x PILE_DENS | D
15 | 15.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 512.9399 |  | 0 | RC_BASE | Model volume | D
15 | 15.05 | Reinforced concrete walls and parapets | m3 | 510.0642 |  | 0 | RC_WALL | Model volume | D
15 | 15.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 348.8402 |  | 0 | RC_SLAB | Model volume | D
15 | 15.07 | Reinforced concrete equipment plinths and pads | m3 | 53.6641 |  | 0 | RC_PLINTH | Model volume | D
15 | 15.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 4944.0605 |  | 0 | FORMWORK | Model face areas | D
15 | 15.09 | High-yield steel reinforcement | t | 175.9359 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
16 |  | Grease pump station
16 | 16.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 437.0837 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
16 | 16.02 | Backfill around structure to NG in compacted layers | m3 | 359.6437 |  | 0 | BACKFILL | Structures sheet | D
16 | 16.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 3 |  | 0 | PILE | Footprint x PILE_DENS | D
16 | 16.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 6.912 |  | 0 | RC_BASE | Model volume | D
16 | 16.05 | Reinforced concrete walls and parapets | m3 | 14.6256 |  | 0 | RC_WALL | Model volume | D
16 | 16.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 1.98 |  | 0 | RC_SLAB | Model volume | D
16 | 16.07 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 2.412 |  | 0 | RC_MISC | Model volume | D
16 | 16.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 121.602 |  | 0 | FORMWORK | Model face areas | D
16 | 16.09 | High-yield steel reinforcement | t | 3.3581 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
17 |  | Scum pump station
17 | 17.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 915.3398 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
17 | 17.02 | Backfill around structure to NG in compacted layers | m3 | 801.5998 |  | 0 | BACKFILL | Structures sheet | D
17 | 17.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 3 |  | 0 | PILE | Footprint x PILE_DENS | D
17 | 17.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 6.912 |  | 0 | RC_BASE | Model volume | D
17 | 17.05 | Reinforced concrete walls and parapets | m3 | 20.5656 |  | 0 | RC_WALL | Model volume | D
17 | 17.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 2.952 |  | 0 | RC_SLAB | Model volume | D
17 | 17.07 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 1.49 |  | 0 | RC_MISC | Model volume | D
17 | 17.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 170.47 |  | 0 | FORMWORK | Model face areas | D
17 | 17.09 | High-yield steel reinforcement | t | 4.1962 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
18 |  | WAS pre-dewatering building
18 | 18.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 0 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
18 | 18.02 | Backfill around structure to NG in compacted layers | m3 | 0 |  | 0 | BACKFILL | Structures sheet | D
18 | 18.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 225 |  | 0 | PILE | Footprint x PILE_DENS | D
18 | 18.04 | Plain concrete blinding / screed | m3 | 383.5399 |  | 0 | BLINDING | Model volume | D
18 | 18.05 | Reinforced concrete rafts, bases, floors and foundations | m3 | 558.5522 |  | 0 | RC_BASE | Model volume | D
18 | 18.06 | Reinforced concrete walls and parapets | m3 | 460.1032 |  | 0 | RC_WALL | Model volume | D
18 | 18.07 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 387.2957 |  | 0 | RC_SLAB | Model volume | D
18 | 18.08 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 17.1871 |  | 0 | RC_MISC | Model volume | D
18 | 18.09 | Reinforced concrete equipment plinths and pads | m3 | 115.9559 |  | 0 | RC_PLINTH | Model volume | D
18 | 18.10 | Formwork to vertical faces and soffits of elevated elements | m2 | 5496.1416 |  | 0 | FORMWORK | Model face areas | D
18 | 18.11 | High-yield steel reinforcement | t | 186.0388 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
19 |  | THP system platform
19 | 19.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 0 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
19 | 19.02 | Backfill around structure to NG in compacted layers | m3 | 0 |  | 0 | BACKFILL | Structures sheet | D
19 | 19.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 124 |  | 0 | PILE | Footprint x PILE_DENS | D
19 | 19.04 | Reinforced concrete equipment plinths and pads | m3 | 616 |  | 0 | RC_PLINTH | Model volume | D
19 | 19.05 | Formwork to vertical faces and soffits of elevated elements | m2 | 70.8 |  | 0 | FORMWORK | Model face areas | D
19 | 19.06 | High-yield steel reinforcement | t | 49.28 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
20 |  | Final dewatering building
20 | 20.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 501.2059 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
20 | 20.02 | Backfill around structure to NG in compacted layers | m3 | 82.1059 |  | 0 | BACKFILL | Structures sheet | D
20 | 20.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 172 |  | 0 | PILE | Footprint x PILE_DENS | D
20 | 20.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 387.7554 |  | 0 | RC_BASE | Model volume | D
20 | 20.05 | Reinforced concrete walls and parapets | m3 | 282.4441 |  | 0 | RC_WALL | Model volume | D
20 | 20.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 161.4337 |  | 0 | RC_SLAB | Model volume | D
20 | 20.07 | Reinforced concrete equipment plinths and pads | m3 | 47.094 |  | 0 | RC_PLINTH | Model volume | D
20 | 20.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 2954.013 |  | 0 | FORMWORK | Model face areas | D
20 | 20.09 | High-yield steel reinforcement | t | 105.7859 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
20 | 20.10 | Doors and glazing envelopes in model - architectural, count for reference | no. | 2 | excluded | 0 | ARCH | Model element count | D
21 |  | CHP building
21 | 21.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 1505.6993 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
21 | 21.02 | Backfill around structure to NG in compacted layers | m3 | 305.0993 |  | 0 | BACKFILL | Structures sheet | D
21 | 21.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 114 |  | 0 | PILE | Footprint x PILE_DENS | D
21 | 21.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 400.1441 |  | 0 | RC_BASE | Model volume | D
21 | 21.05 | Reinforced concrete walls and parapets | m3 | 373.3501 |  | 0 | RC_WALL | Model volume | D
21 | 21.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 210.3918 |  | 0 | RC_SLAB | Model volume | D
21 | 21.07 | Reinforced concrete equipment plinths and pads | m3 | 40.5 |  | 0 | RC_PLINTH | Model volume | D
21 | 21.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 3749.6394 |  | 0 | FORMWORK | Model face areas | D
21 | 21.09 | High-yield steel reinforcement | t | 125.6754 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
22 |  | Chlorination storage building
22 | 22.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 595.2829 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
22 | 22.02 | Backfill around structure to NG in compacted layers | m3 | 229.3229 |  | 0 | BACKFILL | Structures sheet | D
22 | 22.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 33 |  | 0 | PILE | Footprint x PILE_DENS | D
22 | 22.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 63.2191 |  | 0 | RC_BASE | Model volume | D
22 | 22.05 | Reinforced concrete walls and parapets | m3 | 80.0633 |  | 0 | RC_WALL | Model volume | D
22 | 22.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 45.605 |  | 0 | RC_SLAB | Model volume | D
22 | 22.07 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 26.412 |  | 0 | RC_MISC | Model volume | D
22 | 22.08 | Reinforced concrete equipment plinths and pads | m3 | 16.56 |  | 0 | RC_PLINTH | Model volume | D
22 | 22.09 | Formwork to vertical faces and soffits of elevated elements | m2 | 1519.5535 |  | 0 | FORMWORK | Model face areas | D
22 | 22.10 | High-yield steel reinforcement | t | 28.6603 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
23 |  | Air blowers power house
23 | 23.01 | Excavation below NG (-0.70) to underside of lowest element, incl. working space and side slopes; dispose / stockpile | m3 | 0 |  | 0 | EXC | Structures sheet: model footprint and lowest level; WS_STR, SLOPE_STR | D
23 | 23.02 | Backfill around structure to NG in compacted layers | m3 | 0 |  | 0 | BACKFILL | Structures sheet | D
23 | 23.03 | Piles 600 mm diameter (CFA / bored) - length to pile design - ALLOWANCE (no pile layout in model) | no. | 19 |  | 0 | PILE | Footprint x PILE_DENS | D
23 | 23.04 | Reinforced concrete rafts, bases, floors and foundations | m3 | 45.202 |  | 0 | RC_BASE | Model volume | D
23 | 23.05 | Reinforced concrete walls and parapets | m3 | 73.8276 |  | 0 | RC_WALL | Model volume | D
23 | 23.06 | Reinforced concrete suspended slabs, decks, roofs and walkways | m3 | 30.0134 |  | 0 | RC_SLAB | Model volume | D
23 | 23.07 | Reinforced concrete channels, baffles, weirs, chambers, hoppers and secondary elements | m3 | 10.575 |  | 0 | RC_MISC | Model volume | D
23 | 23.08 | Formwork to vertical faces and soffits of elevated elements | m2 | 949.7365 |  | 0 | FORMWORK | Model face areas | D
23 | 23.09 | High-yield steel reinforcement | t | 20.449 |  | 0 | REBAR | Concrete volume x ratio (Inputs) | D
24 |  | Underground pipework - 45 printed lines, 201 packages (DLU-002 Rev 03)
24 | 24.01 | Supply, lay and joint GRP pipe DN2600 | m | 776.6392 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.02 | Supply, lay and joint GRP pipe DN2500 | m | 324.2877 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.03 | Supply, lay and joint GRP pipe DN2400 | m | 990.9326 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.04 | Supply, lay and joint GRP pipe DN2200 | m | 1373.9776 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.05 | Supply, lay and joint GRP pipe DN2000 | m | 1446.5513 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.06 | Supply, lay and joint GRP pipe DN1800 | m | 224.9701 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.07 | Supply, lay and joint HDPE pipe OD1400 | m | 1259.1524 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.08 | Supply, lay and joint HDPE pipe OD1600 | m | 1099.4319 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.09 | Supply, lay and joint HDPE pipe DN1600 as printed | m | 346.3713 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.10 | Supply, lay and joint HDPE pipe OD600 | m | 295.1333 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.11 | Supply, lay and joint HDPE pipe OD500 | m | 13.5454 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.12 | Supply, lay and joint HDPE pipe OD315 | m | 17.8374 |  | 0 | PIPE | Package workbook 3D length | B
24 | 24.13 | GRP fittings - elbow 30 (all sizes) | no. | 27 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.14 | GRP fittings - elbow 45 (all sizes) | no. | 96 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.15 | GRP fittings - elbow 90 (all sizes) | no. | 65 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.16 | GRP fittings - flange (all sizes) | no. | 2 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.17 | GRP fittings - reducer (all sizes) | no. | 12 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.18 | HDPE fittings - elbow 45 (all sizes) | no. | 123 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.19 | HDPE fittings - elbow 90 (all sizes) | no. | 23 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.20 | HDPE fittings - elbow (angle not stated) (all sizes) | no. | 58 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.21 | HDPE fittings - flange (all sizes) | no. | 41 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.22 | HDPE fittings - reducer (all sizes) | no. | 15 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.23 | HDPE fittings - tee (all sizes) | no. | 10 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.24 | HDPE fittings - stub end (all sizes) | no. | 2 |  | 0 | FITTING | Package workbook fittings per package | B
24 | 24.25 | Connection of pipe to structure wall (puddle flange / grouting) | no. | 90 |  | 0 | CONNECT | Tie-in packages + 2 per short connection | C
24 | 24.26 | Excavation in sheet-piled trench, below GWL | m3 | 104633.083 |  | 0 | EXC | Sequence workbook (MAXOC 2.5 m rule) | C
24 | 24.27 | Excavation in dewatered open cut | m3 | 29959.9607 |  | 0 | EXC | Sequence workbook | C
24 | 24.28 | Temporary steel sheet piles: supply / hire, install and extract (incl. walings and struts) | m2 | 116308.6076 |  | 0 | SHEET | Sequence workbook: wall length x depth x SHEET_RATIO | C
24 | 24.29 | Dewatering: install wellpoints / deep wells along trench | m | 8132.4305 |  | 0 | DEWATER | Sequence workbook | C
24 | 24.30 | Dewatering: operate and maintain (package-days of pumping) | pkg-day | 16981 |  | 0 | DEWATER | Sequence workbook programme (just-in-time dewatering) | C
24 | 24.31 | Piles 600 mm diameter under pipe slabs - PLACEHOLDER layout (rows at 3 m) | no. | 5788 |  | 0 | PILE | Sequence workbook placeholder; no pile design | D
24 | 24.32 | Reinforced concrete piled slab and blinding under pipes (0.50 m) | m3 | 11770.1362 |  | 0 | RC_BASE | Sequence workbook | C
24 | 24.33 | Reinforcement to piled slab under pipes | t | 1294.715 |  | 0 | REBAR | Slab volume x RR_PIPESLAB | D
24 | 24.34 | Granular bedding and surround to 0.3 m above crown | m3 | 51302.3561 |  | 0 | SURROUND | Pipes sheet formula | C
24 | 24.35 | Backfill to NG in compacted layers | m3 | 97445.5446 |  | 0 | BACKFILL | Sequence workbook | C
24 | 24.36 | Anchor straps to piled slab where empty pipe can float at final level | m | 601.1171 |  | 0 | ANCHOR | Sequence workbook flotation check (UG-08, UG-09, UG-10) | C
24 | 24.37 | Locate and protect crossing services (trial pits) at listed crossings | no. | 129 |  | 0 | XING | Packages with crossings listed | C
25 |  | Site-wide and provisional items
25 | 25.01 | Untagged model pipes without levels (90 objects, of which untagged length shown) - provisional, line identity to be resolved | m | 125.5 |  | 0 | PIPE | Model volume / pipe area; tagged unresolved pieces (about 335 m) are assumed already in the line lengths | D
25 | 25.02 | Site raising from NG (-0.70) to FL (+1.00) over the developed area, less structure footprints - PROVISIONAL | m3 | 378367.47 |  | 0 | SITEFILL | Convex hull of model; replace with surveyed site area and levels | D

## Inputs
Inputs and assumptions
Yellow = edit. Quantities in the BOQ recalculate from these values. Rates are entered on the BOQ sheet.
Name | Description | Value | Unit | Source / status
General
CURRENCY | Currency of rates | EGP |  | Enter rates in this currency on the BOQ sheet.
NG | Adopted natural ground level | -0.7 | m | Package workbook D-004 (Mohamed, 20 Oct 2026).
FL | Finished ground level | 1 | m | Package workbook D-004.
Earthworks to structures
WS_STR | Working space around structure footprint at formation | 1 | m | Same as agreed for pipes (21 Oct 2026).
SLOPE_STR | Excavation side slope (H per 1 V); 0 = vertical (shored) | 1.5 | H:V | ASSUMPTION - soft silty clay. Temporary works design governs.
Piling
PILE_DENS | Allowance where the model has no piles: Ø600 piles per m2 of footprint | 0.1 | no./m2 | Calibrated to aeration: 3,672 modelled piles / 34,995 m2 footprint = 0.105. ALLOWANCE only.
Reinforcement ratios (kg per m3 of concrete) - ASSUMPTIONS unless noted
RR_BASE | Rafts, bases and foundations | 107 | kg/m3 | Aeration raft estimate 3,203 t / 30,012 m3 (model text "AW-AER Tracking Documentation", incl. 10% laps and 10% extra bars).
RR_WALL | Walls and parapets | 140 | kg/m3 | ASSUMPTION - water-retaining walls.
RR_SLAB | Suspended slabs, decks, roofs, walkways | 130 | kg/m3 | ASSUMPTION.
RR_COLBEAM | Columns, beams, piers | 180 | kg/m3 | ASSUMPTION.
RR_MISC | Channels, baffles, weirs, chambers, hoppers | 130 | kg/m3 | ASSUMPTION.
RR_PLINTH | Equipment plinths and pads | 80 | kg/m3 | ASSUMPTION.
RR_BRIDGE | Concrete bridge members (thickeners) | 200 | kg/m3 | ASSUMPTION - slender bridge members. Bridge is concrete (Mohamed, 22 Oct 2026); model collection is labelled "Steel truss".
RR_PIPESLAB | Piled slab under pipes | 110 | kg/m3 | ASSUMPTION - no slab design.
Steel and metalwork
STEEL_DENS | Density of steel | 7.85 | t/m3 | Physical constant; applied to modelled steel member volume.
RAILS_PER_RUN | Rail members per handrail run (top + knee rail) | 2 | no. | ASSUMPTION - modelled rails are individual members.
Underground pipework
WS_PIPE | Working space each side of pipe (trench bottom width = OD + 2 x WS) | 1 | m | AGREED 21 Oct 2026.
SURR_ABOVE | Granular surround above pipe crown | 0.3 | m | ASSUMPTION.
Site-wide provisional
SITE_AREA | Developed area for site raising (convex hull of all modelled assets) | 312422 | m2 | Computed from the 3D model; site boundary not in the model - replace with surveyed area.
SITE_DEDUCT | Deduct footprint of structures from site raising (1 = yes) | 1 | -

## Take-off
Take-off from the 3D coordination model (Alex-West-Combined-Coordination.blend, 19 Oct 2026)
One row per structure / element class. Volumes and areas are measured on closed model solids (all 15,195 meshes are closed). Formwork = vertical faces + soffits of elevated elements. Blue = model data; the BOQ sums these rows.
Bill | Asset | Element class | Elements (no.) | Volume (m3) | Top area (m2) | Formwork area (m2) | Rail member length (m) | Lowest level (m) | Element names (sample)
GRT | AW-GRT | HANDRAIL | 71 | 0.48918 | 0.11366 | 0 | 238.6 | 6.3 | Perimeter post; Perimeter rail; Raised walkway handrail; Raised walkway post
GRT | AW-GRT | MASS_FILL | 32 | 273.4294 | 150.6572 | 0 | 0 | 0.5 | G1 floor slope 1-; G1 floor slope 2-; G2 floor slope 1-; G2 floor slope 2-; G3 floor slope 1-; G3 floor slope 2-
GRT | AW-GRT | RC_BASE | 7 | 489.2294 | 647.3158 | 192.3206 | 0 | -5.7 | Deep outlet well base; Grit common raft; Pair 1 inlet distributor floor; Pair 2 inlet distributor floor; Rejected bypass floor envelope; Screen common floor
GRT | AW-GRT | RC_MISC | 58 | 31.329 | 28.7261 | 448.8004 | 0 | -5.2 | Deep outlet well west below screen; G1 GRP stilling baffle; G1 inlet distributor cheek; G1 scum trough bottom; G1 scum trough side; G2 GRP stilling baffle
GRT | AW-GRT | RC_SLAB | 21 | 224.8037 | 511.1383 | 736.2501 | 0 | 2.5 | Deep outlet well access deck; Flume internal walkway; G1 lane walkway; G2 lane walkway; G3 lane walkway; G4 lane walkway
GRT | AW-GRT | RC_WALL | 42 | 967.4698 | 298.5626 | 3532.0884 | 0 | -5.2 | Deep outlet well east wall; Deep outlet well north wall; Deep outlet well south wall; Drawn flume wall -4.45; Drawn flume wall -6.45; Full dividing wall
GRT | AW-GRT | STAIRS | 38 | 41.3814 | 10.2599 | 0 | 0 | -1.37 | Southwest stair tread
PST | AW-PST | BLINDING | 17 | 1104.2745 | 5587.3875 | 0 | 0 | -2.2 | Basin 01 hopper transverse screed; Basin 02 hopper transverse screed; Basin 03 hopper transverse screed; Basin 04 hopper transverse screed; Basin 05 hopper transverse screed; Basin 06 hopper transverse screed
PST | AW-PST | HANDRAIL | 576 | 4.5462 | 0.92143 | 0 | 2243.2 | 4 | Basin 01 walkway rail; Basin 01 walkway rail post; Basin 02 walkway rail; Basin 02 walkway rail post; Basin 03 walkway rail; Basin 03 walkway rail post
PST | AW-PST | MASS_FILL | 8 | 317.3132 | 403.3664 | 0 | 0 | -0.93 | Basin 01 outlet-zone sloping fill; Basin 02 outlet-zone sloping fill; Basin 03 outlet-zone sloping fill; Basin 04 outlet-zone sloping fill; Basin 05 outlet-zone sloping fill; Basin 06 outlet-zone sloping fill
PST | AW-PST | RC_BASE | 86 | 6012.3696 | 6454.3794 | 971.7728 | 0 | -7.6 | Basin 01 outlet finger base; Basin 01 sloping hopper slab; Basin 01 sludge trough base; Basin 02 outlet finger base; Basin 02 sloping hopper slab; Basin 02 sludge trough base
PST | AW-PST | RC_COLBEAM | 88 | 47.6065 | 20.88 | 392.16 | 0 | -0.63 | Basin 01 baffle pier; Basin 02 baffle pier; Basin 03 baffle pier; Basin 04 baffle pier; Basin 05 baffle pier; Basin 06 baffle pier
PST | AW-PST | RC_MISC | 18 | 356.3057 | 430.747 | 1897.8236 | 0 | -0.93 | Basin 01 baffle header; Basin 01 baffle sill; Basin 02 baffle header; Basin 02 baffle sill; Basin 03 baffle header; Basin 03 baffle sill
PST | AW-PST | RC_SLAB | 22 | 267.2185 | 1336.0925 | 1750.9513 | 0 | 3.8 | Basin 01 inlet access deck; Basin 02 inlet access deck; Basin 03 inlet access deck; Basin 04 inlet access deck; Basin 05 inlet access deck; Basin 06 inlet access deck
PST | AW-PST | RC_WALL | 175 | 2144.7301 | 646.9117 | 10296.562 | 0 | -7.3 | Basin 01 outlet finger wall; Basin 01 sludge trough end wall; Basin 01 sludge trough outer wall; Basin 02 outlet finger wall; Basin 02 sludge trough end wall; Basin 02 sludge trough outer wall
PST | AW-PST | STAIRS | 90 | 64.0469 | 22.1997 | 0 | 0 | -1.35 | East outlet stair tread; West inlet stair tread; West outlet stair tread
IPS | AW-IPS | RC_BASE | 14 | 638.9607 | 801.495 | 432.8739 | 0 | -7.6 | Bypass raft; IPS CH01 sloping base; IPS CH02 sloping base; IPS CH03 sloping base; IPS CH04 sloping base; IPS CH05 sloping base
IPS | AW-IPS | RC_SLAB | 2 | 102.5692 | 356.8972 | 395.2716 | 0 | 3.2 | IPS electrical roof slab; Inlet deck OP01 and OP02 access openings
IPS | AW-IPS | RC_WALL | 21 | 1064.5933 | 203.9344 | 3169.2882 | 0 | -6.6 | Bypass external wall with two nominal pipe penetrations; Bypass transverse partition; IPS approach sidewall; IPS divider; IPS electrical end wall; IPS electrical long wall
IPS | AW-IPS | STAIRS | 330 | 47.0063 | 232.5604 | 0 | 0 | 3.12 | Indicative stair tread; Indicative stair waist; Upper IPS landing
IPS | AW-IPS-SHARED | RC_BASE | 2 | 137.3221 | 321.5554 | 57.9921 | 0 | 3.5 | Motor hall floor; Outlet extension base
IPS | AW-IPS-SHARED | RC_MISC | 9 | 223.0756 | 26.7586 | 121.1803 | 0 | 3.5 | IPS CH01 discharge transition; IPS CH02 discharge transition; IPS CH03 discharge transition; IPS CH04 discharge transition; IPS CH05 discharge transition; IPS CH06 discharge transition
IPS | AW-IPS-SHARED | RC_SLAB | 2 | 268.8312 | 701.4131 | 755.798 | 0 | 3.5 | Motor hall roof slab; Shared distribution slab
IPS | AW-IPS-SHARED | RC_WALL | 11 | 363.5057 | 92.7804 | 1471.5617 | 0 | 4.3 | Motor hall end wall; Motor hall longitudinal upper wall; Outlet extension sidewall; Roof parapet - CAD envelope; Shared distribution divider
AER | AW-AER | HANDRAIL | 1624 | 15.9936 | 280.4144 | 0 | 6160.2001 | 8.2 | Axis1 post; Axis1 rail; Axis10 post; Axis10 rail; Axis2 post; Axis2 rail
AER | AW-AER | PILE | 3672 | 4107.7341 | 1011.752 | 0 | 0 | -3.8 | P0001 dia600 - truncated; P0002 dia600 - truncated; P0003 dia600 - truncated; P0004 dia600 - truncated; P0005 dia600 - truncated; P0006 dia600 - truncated
AER | AW-AER | RC_BASE | 14 | 30119.834 | 33611.2716 | 2128.1576 | 0 | -3.1 | Distribution chamber context raft; North inlet segment1 raft extension; North inlet segment2 raft extension; North inlet segment3 raft extension; North inlet segment4 raft extension; Northwest turn floor
AER | AW-AER | RC_COLBEAM | 324 | 209.0851 | 70.9644 | 1722.2865 | 0 | 1.15 | C1-C2-001 400 square; C1-C2-002 400 square; C1-C2-003 400 square; C1-C2-004 400 square; C1-C2-005 400 square; C1-C2-006 400 square
AER | AW-AER | RC_MISC | 118 | 5183.7867 | 6045.3586 | 20291.0683 | 0 | 1.15 | Basin 1 baffle 1 with openings; Basin 1 baffle 2 with openings; Basin 1 baffle 3 with openings; Basin 1 baffle 4 with openings; Basin 2 baffle 1 with openings; Basin 2 baffle 2 with openings
AER | AW-AER | RC_SLAB | 54 | 764.2811 | 3820.0883 | 4805.0083 | 0 | 8 | Axis1 1200 walk slab; Axis10 1200 walk slab; Axis3 1200 walk slab; Axis5 1200 walk slab; Axis6 1200 walk slab; Axis8 1200 walk slab
AER | AW-AER | RC_WALL | 91 | 12805.6583 | 2046.1487 | 35541.1517 | 0 | -2.7 | Axis 1 tapered wall; Axis 10 tapered wall; Axis 2 tapered wall; Axis 3 tapered wall; Axis 4 tapered wall; Axis 5 tapered wall
AER | AW-AER | STAIRS | 15 | 8.6025 | 38.1003 | 0 | 0 | 0.8 | Stair1 east flight; Stair1 east landing; Stair2 north flight; Stair2 north landing; Stair3 west flight; Stair3 west landing
SDC | AW-SDC-A | BLINDING | 2 | 74.0921 | 246.9737 | 0 | 0 | -5.7 | Deep-well blinding envelope; Outer slab blinding envelope
SDC | AW-SDC-A | HANDRAIL | 104 | 0.38556 | 0.16639 | 0 | 170.5918 | 1 | Indicative perimeter post; Indicative perimeter rail; Indicative stair post; Indicative stair rail
SDC | AW-SDC-A | RC_BASE | 2 | 138.0232 | 230.0386 | 72.8502 | 0 | -5.4 | Deep well base slab; Octagonal outlet floor slab
SDC | AW-SDC-A | RC_MISC | 1 | 124.757 | 13.5115 | 624.5007 | 0 | -4.8 | Circular well and overflow weir
SDC | AW-SDC-A | RC_SLAB | 11 | 21.5829 | 80.0624 | 137.4808 | 0 | 1 | Indicative landing support; Perimeter walkway 1.20 m nominal; Radial walkway; Widened baffle head
SDC | AW-SDC-A | RC_WALL | 5 | 117.2761 | 26.2303 | 601.3298 | 0 | 1 | Compartment divider; Octagonal outer wall with four PD02 holes
SDC | AW-SDC-A | STAIRS | 2 | 3.5539 | 12.6 | 0 | 0 | 1 | External three-flight stair with two intermediate landings; Inner ladder landing extension
SDC | AW-SDC-B | BLINDING | 2 | 74.0921 | 246.9737 | 0 | 0 | -5.7 | Deep-well blinding envelope; Outer slab blinding envelope
SDC | AW-SDC-B | HANDRAIL | 104 | 0.38559 | 0.16641 | 0 | 170.5918 | 1 | Indicative perimeter post; Indicative perimeter rail; Indicative stair post; Indicative stair rail
SDC | AW-SDC-B | RC_BASE | 2 | 138.0232 | 230.0386 | 72.8502 | 0 | -5.4 | Deep well base slab; Octagonal outlet floor slab
SDC | AW-SDC-B | RC_MISC | 1 | 124.7568 | 13.5114 | 624.5008 | 0 | -4.8 | Circular well and overflow weir
SDC | AW-SDC-B | RC_SLAB | 11 | 21.5829 | 80.0625 | 137.4808 | 0 | 1 | Indicative landing support; Perimeter walkway 1.20 m nominal; Radial walkway; Widened baffle head
SDC | AW-SDC-B | RC_WALL | 5 | 117.276 | 26.2303 | 601.3299 | 0 | 1 | Compartment divider; Octagonal outer wall with four PD02 holes
SDC | AW-SDC-B | STAIRS | 2 | 3.5539 | 12.6 | 0 | 0 | 1 | External three-flight stair with two intermediate landings; Inner ladder landing extension
SDC | AW-SDC-C | BLINDING | 2 | 74.0921 | 246.9737 | 0 | 0 | -5.7 | Deep-well blinding envelope; Outer slab blinding envelope
SDC | AW-SDC-C | HANDRAIL | 104 | 0.38557 | 0.16638 | 0 | 170.5918 | 1 | Indicative perimeter post; Indicative perimeter rail; Indicative stair post; Indicative stair rail
SDC | AW-SDC-C | RC_BASE | 2 | 138.0232 | 230.0387 | 72.8502 | 0 | -5.4 | Deep well base slab; Octagonal outlet floor slab
SDC | AW-SDC-C | RC_MISC | 1 | 124.7572 | 13.5115 | 624.5011 | 0 | -4.8 | Circular well and overflow weir
SDC | AW-SDC-C | RC_SLAB | 11 | 21.583 | 80.063 | 137.4813 | 0 | 1 | Indicative landing support; Perimeter walkway 1.20 m nominal; Radial walkway; Widened baffle head
SDC | AW-SDC-C | RC_WALL | 5 | 117.2762 | 26.2303 | 601.3301 | 0 | 1 | Compartment divider; Octagonal outer wall with four PD02 holes
SDC | AW-SDC-C | STAIRS | 2 | 3.5539 | 12.6 | 0 | 0 | 1 | External three-flight stair with two intermediate landings; Inner ladder landing extension
FST | AW-FST-A | BLINDING | 6 | 269.4591 | 2696.1292 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-A | PILE | 213 | 178.6192 | 59.5398 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-A | RC_BASE | 8 | 1861.5167 | 2668.1215 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-A | RC_COLBEAM | 12 | 3.2414 | 5.4024 | 24.9568 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-A | RC_MISC | 12 | 91.5341 | 147.1611 | 365.367 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-A | RC_SLAB | 4 | 88.3495 | 323.4579 | 430.1798 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-A | RC_WALL | 9 | 675.4835 | 321.6529 | 2470.7262 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-A | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-B | BLINDING | 6 | 269.4591 | 2696.1288 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-B | PILE | 213 | 178.6166 | 59.5389 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-B | RC_BASE | 8 | 1861.5168 | 2668.1215 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-B | RC_COLBEAM | 12 | 3.2414 | 5.4023 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-B | RC_MISC | 12 | 91.5338 | 147.161 | 365.3674 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-B | RC_SLAB | 4 | 88.3495 | 323.458 | 430.1799 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-B | RC_WALL | 9 | 675.4837 | 321.653 | 2470.7263 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-B | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-C | BLINDING | 6 | 269.4591 | 2696.1301 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-C | PILE | 213 | 178.6179 | 59.5393 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-C | RC_BASE | 8 | 1861.5168 | 2668.1222 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-C | RC_COLBEAM | 12 | 3.2414 | 5.4023 | 24.957 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-C | RC_MISC | 12 | 91.5335 | 147.161 | 365.3671 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-C | RC_SLAB | 4 | 88.3495 | 323.4585 | 430.1804 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-C | RC_WALL | 9 | 675.4838 | 321.653 | 2470.7265 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-C | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-D | BLINDING | 6 | 269.4591 | 2696.1308 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-D | PILE | 213 | 178.6185 | 59.5397 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-D | RC_BASE | 8 | 1861.5169 | 2668.1232 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-D | RC_COLBEAM | 12 | 3.2414 | 5.4024 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-D | RC_MISC | 12 | 91.5336 | 147.1613 | 365.3671 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-D | RC_SLAB | 4 | 88.3495 | 323.4582 | 430.1801 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-D | RC_WALL | 9 | 675.4834 | 321.6526 | 2470.726 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-D | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-E | BLINDING | 6 | 269.4591 | 2696.1293 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-E | PILE | 213 | 178.6182 | 59.5393 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-E | RC_BASE | 8 | 1861.5169 | 2668.1217 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-E | RC_COLBEAM | 12 | 3.2414 | 5.4024 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-E | RC_MISC | 12 | 91.5336 | 147.1612 | 365.3669 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-E | RC_SLAB | 4 | 88.3495 | 323.4579 | 430.1799 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-E | RC_WALL | 9 | 675.4831 | 321.6529 | 2470.726 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-E | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-F | BLINDING | 6 | 269.4591 | 2696.1293 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-F | PILE | 213 | 178.6183 | 59.5396 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-F | RC_BASE | 8 | 1861.5168 | 2668.1217 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-F | RC_COLBEAM | 12 | 3.2414 | 5.4023 | 24.9568 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-F | RC_MISC | 12 | 91.5341 | 147.1612 | 365.3672 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-F | RC_SLAB | 4 | 88.3495 | 323.458 | 430.1799 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-F | RC_WALL | 9 | 675.4834 | 321.6528 | 2470.7264 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-F | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-G | BLINDING | 6 | 269.4591 | 2696.1272 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-G | PILE | 213 | 178.6181 | 59.5395 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-G | RC_BASE | 8 | 1861.5168 | 2668.1199 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-G | RC_COLBEAM | 12 | 3.2414 | 5.4024 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-G | RC_MISC | 12 | 91.5339 | 147.1622 | 365.3671 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-G | RC_SLAB | 4 | 88.3495 | 323.4577 | 430.1798 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-G | RC_WALL | 9 | 675.4837 | 321.6532 | 2470.7264 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-G | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-H | BLINDING | 6 | 269.4591 | 2696.1295 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-H | PILE | 213 | 178.619 | 59.5397 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-H | RC_BASE | 8 | 1861.5168 | 2668.1219 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-H | RC_COLBEAM | 12 | 3.2414 | 5.4023 | 24.9568 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-H | RC_MISC | 12 | 91.5343 | 147.1612 | 365.3672 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-H | RC_SLAB | 4 | 88.3495 | 323.4579 | 430.1797 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-H | RC_WALL | 9 | 675.4838 | 321.653 | 2470.7263 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-H | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-I | BLINDING | 6 | 269.4591 | 2696.1292 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-I | PILE | 213 | 178.6165 | 59.5389 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-I | RC_BASE | 8 | 1861.5169 | 2668.1217 | 249.6371 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-I | RC_COLBEAM | 12 | 3.2414 | 5.4023 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-I | RC_MISC | 12 | 91.5336 | 147.1611 | 365.3673 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-I | RC_SLAB | 4 | 88.3495 | 323.4578 | 430.1797 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-I | RC_WALL | 9 | 675.4827 | 321.6528 | 2470.7264 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-I | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-J | BLINDING | 6 | 269.4591 | 2696.1285 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-J | PILE | 213 | 178.618 | 59.5393 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-J | RC_BASE | 8 | 1861.5169 | 2668.121 | 249.6371 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-J | RC_COLBEAM | 12 | 3.2414 | 5.4024 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-J | RC_MISC | 12 | 91.5336 | 147.1612 | 365.3674 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-J | RC_SLAB | 4 | 88.3495 | 323.4579 | 430.1798 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-J | RC_WALL | 9 | 675.4833 | 321.6527 | 2470.7261 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-J | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-K | BLINDING | 6 | 269.4591 | 2696.1291 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-K | PILE | 213 | 178.6166 | 59.5389 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-K | RC_BASE | 8 | 1861.5169 | 2668.1216 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-K | RC_COLBEAM | 12 | 3.2414 | 5.4024 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-K | RC_MISC | 12 | 91.5336 | 147.1611 | 365.3672 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-K | RC_SLAB | 4 | 88.3495 | 323.4579 | 430.1799 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-K | RC_WALL | 9 | 675.4831 | 321.6528 | 2470.7261 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-K | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
FST | AW-FST-L | BLINDING | 6 | 269.4591 | 2696.1293 | 0 | 0 | -4.5 | 100 mm blinding beneath raft; DN1000 support blinding; DN1600 support blinding; Drain chamber blinding; Hopper base blinding; Outlet chamber blinding
FST | AW-FST-L | PILE | 213 | 178.617 | 59.539 | 0 | 0 | -7.4 | P001 — diameter600 display stub; P002 — diameter600 display stub; P003 — diameter600 display stub; P004 — diameter600 display stub; P005 — diameter600 display stub; P006 — diameter600 display stub
FST | AW-FST-L | RC_BASE | 8 | 1861.5169 | 2668.1218 | 249.6372 | 0 | -4.4 | DN1000 support foundation beam; DN1600 support foundation beam; Drain chamber base — 500 mm; Hopper base — 700 mm; Outlet chamber base — 500 mm; Sloping 700 mm annular raft
FST | AW-FST-L | RC_COLBEAM | 12 | 3.2414 | 5.4023 | 24.9569 | 0 | 1.85 | Feedwell pier; Hopper pier
FST | AW-FST-L | RC_MISC | 12 | 91.5337 | 147.1612 | 365.3672 | 0 | -3.9 | C1 circular support; DN1000 support concrete cradle; DN1600 support concrete cradle; Drain chamber side; Drain chamber side -; Feedwell lower cylinder
FST | AW-FST-L | RC_SLAB | 4 | 88.3495 | 323.4579 | 430.1798 | 0 | 2.45 | 250 mm perimeter walkway; Central annular transfer slab — 400 mm; Feedwell cap — 400 mm; Outlet chamber roof with 1000 x 1000 hatch
FST | AW-FST-L | RC_WALL | 9 | 675.4832 | 321.6528 | 2470.7262 | 0 | -3.9 | 600 mm perimeter wall; Baffle upper wall — 300 mm; Drain chamber inner wall below raft; Drain chamber outer wall; Hopper lower wall; Outlet chamber inner wall below raft
FST | AW-FST-L | STAIRS | 29 | 4.1583 | 10.9597 | 0 | 0 | 0.2 | Intermediate stair landing; Stair 1 tread; Stair 2 tread; Stair B1 — 250 x; Stair C2 — 400 x; Stair starter
RAS | AW-RASWAS | RC_BASE | 13 | 404.6505 | 525.8425 | 292.1914 | 0 | -9 | RAS CH01 sloping base; RAS CH02 sloping base; RAS CH03 sloping base; RAS CH04 sloping base; RAS CH05 sloping base; RAS CH06 sloping base
RAS | AW-RASWAS | RC_SLAB | 2 | 65.2814 | 233.1046 | 268.0177 | 0 | 4.2 | RAS WAS top deck with access and pump discharge openings; RAS electrical room roof
RAS | AW-RASWAS | RC_WALL | 16 | 969.1038 | 149.2544 | 2898.741 | 0 | -8 | RAS WAS external wet well wall PD04 PD; RAS approach end wall; RAS divider; RAS electrical room end/partition wall; RAS electrical room longitudinal wall; RAS wet well front lower wall
CCT | AW-CCT | BLINDING | 1 | 720.69 | 3603.45 | 0 | 0 | -1.01 | Main raft blinding
CCT | AW-CCT | HANDRAIL | 138 | 1.2185 | 0.27944 | 0 | 469.4279 | 1 | Central north post; Central north rail 0; Central north rail 1; Central south post; Central south rail 0; Central south rail 1
CCT | AW-CCT | RC_BASE | 7 | 2676.7586 | 6762.2192 | 277.6202 | 0 | -6.6 | Drain sump 1 thickened base; Drain sump 2 thickened base; Inlet chamber raft; Main contact tank raft; Outlet well raft; TK-0801A longitudinal sloping floor
CCT | AW-CCT | RC_MISC | 31 | 349.2759 | 92.3219 | 2874.229 | 0 | -6.5 | Collector side weir; East North overflow weir; East South overflow weir; Inlet local sump shell; TK-0801A baffle; TK-0801B baffle
CCT | AW-CCT | RC_SLAB | 6 | 40.56 | 202.8 | 260.48 | 0 | 3.6 | Central access spine; Inlet access bridge; Inlet long access strip; Outlet long access strip; Outlet well inspection bridge; Sampling platform
CCT | AW-CCT | RC_WALL | 68 | 1000.6885 | 224.1385 | 4784.6068 | 0 | -6 | Central dividing wall; Curved wall return; East North perimeter wall; East South perimeter wall; Inlet east deep wall; Inlet north wall
CCT | AW-CCT | STAIRS | 127 | 3.5794 | 9.7228 | 0 | 0 | -6.0175 | Inlet access step; Inlet ladder rung; Inlet ladder stile; Outlet access step; Outlet ladder rung; Outlet ladder stile
FIRE | AW-FIRE | ARCH | 18 | 0.71998 | 0.71997 | 0 | 0 | 6 | Flow hall high window; Pump hall high window
FIRE | AW-FIRE | EQUIP | 28 | 7.5345 | 23.6099 | 0 | 0 | 4.85 | Flow hall crane runway; Flow hall indicative bridge; Flow hall runway corbel; Pump hall crane runway; Pump hall indicative bridge; Pump hall runway corbel
FIRE | AW-FIRE | HANDRAIL | 108 | 0.62375 | 1.9812 | 0 | 209.9111 | -4 | Distribution north post; Distribution north rail 0; Distribution north rail 1; Distribution south post; Distribution south rail 0; Distribution south rail 1
FIRE | AW-FIRE | RC_BASE | 11 | 352.832 | 709.8452 | 190.09 | 0 | -6.5 | Deep overflow south raft; Deep west inlet raft; Distribution channel main raft; Distribution inlet depressed raft; Flow hall drain sump base; Flow hall raft
FIRE | AW-FIRE | RC_COLBEAM | 22 | 35.7199 | 4.4 | 324.28 | 0 | -4 | Flow hall column 12.2/-0; Flow hall column 12.2/9; Flow hall column 17.2/-0; Flow hall column 17.2/9; Flow hall column 22.2/-0; Flow hall column 22.2/9
FIRE | AW-FIRE | RC_MISC | 5 | 24.855 | 5.46 | 234.8499 | 0 | -4 | Maneuvering North overflow weir; Maneuvering South overflow weir; Maneuvering West overflow weir; Outlet well overflow weir
FIRE | AW-FIRE | RC_PLINTH | 7 | 5.2875 | 26.4375 | 9.8 | 0 | -4 | Cooling pump pad; Fire fighting skid pad; Service pump pad
FIRE | AW-FIRE | RC_SLAB | 13 | 233.07 | 582.42 | 687.67 | 0 | -0.15 | Distribution operating deck; Flow hall entrance landing; Flow hall roof slab; Maneuvering North raised shelf; Maneuvering South raised shelf; Maneuvering West raised shelf
FIRE | AW-FIRE | RC_WALL | 35 | 902.2027 | 150.369 | 4719.5397 | 0 | -6 | Distribution channel east wall; Distribution channel west wall; Distribution south wall; East perimeter tank and pump wall; Fire A / Fire B partition; Fire B / Cooling partition
FIRE | AW-FIRE | STAIRS | 9 | 7.791 | 27.47 | 0 | 0 | -5.2 | Distribution sump riser; External west access; External west landing; Flow hall lower flight; Flow hall upper flight; Flow stair intermediate landing
BLOW | AW-BLOW | ARCH | 2 | 2.1099 | 0.44999 | 0 | 0 | 1.2 | Personnel door envelope; Sliding loading-door panel - open position
BLOW | AW-BLOW | BLINDING | 1 | 34.7361 | 347.3609 | 0 | 0 | 0.7 | Floor blinding envelope
BLOW | AW-BLOW | EQUIP | 24 | 124.6654 | 74.0499 | 0 | 0 | 1.4 | Blower-01 acoustic cabinet envelope; Blower-01 discharge silencer envelope; Blower-02 acoustic cabinet envelope; Blower-02 discharge silencer envelope; Blower-03 acoustic cabinet envelope; Blower-03 discharge silencer envelope
BLOW | AW-BLOW | RC_BASE | 1 | 135.3761 | 338.4403 | 100.1692 | 0 | 0.8 | Ground floor slab
BLOW | AW-BLOW | RC_COLBEAM | 40 | 73.2998 | 50.7999 | 552.3993 | 0 | 1.2 | East roof edge beam; Guide column; Guide column 01 corbel; Guide column 02 corbel; Guide column 03 corbel; Guide column 04 corbel
BLOW | AW-BLOW | RC_MISC | 6 | 63.3102 | 105.3996 | 441.489 | 0 | -0.05 | Cable trench 1 RC shell; Cable trench 2 RC shell; Cable trench 3 RC shell; Cable trench 4 RC shell; Cable trench 5 RC shell; Cable trench 6 RC shell
BLOW | AW-BLOW | RC_PLINTH | 10 | 15 | 75.0001 | 22 | 0 | 1.2 | Blower-01 plinth; Blower-02 plinth; Blower-03 plinth; Blower-04 plinth; Blower-05 plinth; Blower-06 plinth
BLOW | AW-BLOW | RC_SLAB | 8 | 96.8767 | 529.2862 | 558.5554 | 0 | 0.8 | Cable trench 1 removable cover; Cable trench 2 removable cover; Cable trench 3 removable cover; Cable trench 4 removable cover; Cable trench 5 removable cover; Cable trench 6 removable cover
BLOW | AW-BLOW | RC_WALL | 8 | 259.8236 | 44.6105 | 1832.3597 | 0 | 1.2 | East parapet; East wall; North parapet; North wall; South parapet; South wall
THK | AW-THK-A | BLINDING | 1 | 98.1573 | 486.8694 | 0 | 0 | -1.37 | 150mm blinding and 50mm screed envelope
THK | AW-THK-A | GRATING | 1 | 0.21222 | 35.37 | 0 | 0 | 5.175 | 6mm chequer plate bridge deck
THK | AW-THK-A | HANDRAIL | 28 | 0.11687 | 0.056686 | 0 | 35.7239 | 1 | Indicative rail post; Indicative stair rail
THK | AW-THK-A | PILE | 41 | 42.3156 | 11.5179 | 0 | 0 | -3.8 | P01 dia600 - display stub; P02 dia600 - display stub; P03 dia600 - display stub; P04 dia600 - display stub; P05 dia600 - display stub; P06 dia600 - display stub
THK | AW-THK-A | RC_BASE | 4 | 307.6171 | 508.7785 | 69.0688 | 0 | -1.17 | 600mm raft with sloping floor and integral hopper; Bridge foundation tab; Bridge foundation tab -; Stair foundation slab
THK | AW-THK-A | RC_BRIDGE | 104 | 5.3304 | 1.29 | 171.0656 | 0 | 5.025 | B1 diagonal -0.75; B1 diagonal 0.75; B3 chord y-0.75 z5; B3 chord y-0.75 z7; B3 chord y0.75 z5; B3 chord y0.75 z7
THK | AW-THK-A | RC_COLBEAM | 6 | 6.876 | 4.96 | 57.5197 | 0 | 0.5 | C2 -1 -0; C2 -1 0; C2 1 -0; C2 1 0; Ground beam 14; Ground beam 15
THK | AW-THK-A | RC_MISC | 1 | 36.6275 | 91.5688 | 155.2775 | 0 | 3.1 | Cantilever channel invert - 400mm
THK | AW-THK-A | RC_SLAB | 4 | 1.65 | 7.25 | 12.9301 | 0 | 2.975 | Bridge bearing head; Bridge bearing head -; Intermediate landing +3; Upper landing +5
THK | AW-THK-A | RC_WALL | 2 | 204.8585 | 77.2696 | 764.9436 | 0 | 0.5 | 600mm circular tank wall - clear diameter 23m; Channel outer wall - 400mm
THK | AW-THK-A | STAIRS | 8 | 5.6984 | 8.7 | 0 | 0 | 0.5 | Stair C1 14.1 -1; Stair C1 14.1 0; Stair C1 14.1 5; Stair C1 15.9 -1; Stair C1 15.9 0; Stair C1 15.9 5
THK | AW-THK-B | BLINDING | 1 | 98.1572 | 486.8696 | 0 | 0 | -1.37 | 150mm blinding and 50mm screed envelope
THK | AW-THK-B | GRATING | 1 | 0.21222 | 35.3701 | 0 | 0 | 5.175 | 6mm chequer plate bridge deck
THK | AW-THK-B | HANDRAIL | 28 | 0.11687 | 0.056686 | 0 | 35.7239 | 1 | Indicative rail post; Indicative stair rail
THK | AW-THK-B | PILE | 41 | 42.3162 | 11.518 | 0 | 0 | -3.8 | P01 dia600 - display stub; P02 dia600 - display stub; P03 dia600 - display stub; P04 dia600 - display stub; P05 dia600 - display stub; P06 dia600 - display stub
THK | AW-THK-B | RC_BASE | 4 | 307.6169 | 508.7785 | 69.0687 | 0 | -1.17 | 600mm raft with sloping floor and integral hopper; Bridge foundation tab; Bridge foundation tab -; Stair foundation slab
THK | AW-THK-B | RC_BRIDGE | 104 | 5.3303 | 1.29 | 171.0635 | 0 | 5.025 | B1 diagonal -0.75; B1 diagonal 0.75; B3 chord y-0.75 z5; B3 chord y-0.75 z7; B3 chord y0.75 z5; B3 chord y0.75 z7
THK | AW-THK-B | RC_COLBEAM | 6 | 6.876 | 4.96 | 57.5199 | 0 | 0.5 | C2 -1 -0; C2 -1 0; C2 1 -0; C2 1 0; Ground beam 14; Ground beam 15
THK | AW-THK-B | RC_MISC | 1 | 36.6276 | 91.5689 | 155.2776 | 0 | 3.1 | Cantilever channel invert - 400mm
THK | AW-THK-B | RC_SLAB | 4 | 1.65 | 7.25 | 12.93 | 0 | 2.975 | Bridge bearing head; Bridge bearing head -; Intermediate landing +3; Upper landing +5
THK | AW-THK-B | RC_WALL | 2 | 204.8584 | 77.2695 | 764.9436 | 0 | 0.5 | 600mm circular tank wall - clear diameter 23m; Channel outer wall - 400mm
THK | AW-THK-B | STAIRS | 8 | 5.6984 | 8.7 | 0 | 0 | 0.5 | Stair C1 14.1 -1; Stair C1 14.1 0; Stair C1 14.1 5; Stair C1 15.9 -1; Stair C1 15.9 0; Stair C1 15.9 5
THK | AW-THK-C | BLINDING | 1 | 98.1572 | 486.8691 | 0 | 0 | -1.37 | 150mm blinding and 50mm screed envelope
THK | AW-THK-C | GRATING | 1 | 0.21222 | 35.3699 | 0 | 0 | 5.175 | 6mm chequer plate bridge deck
THK | AW-THK-C | HANDRAIL | 28 | 0.11689 | 0.056703 | 0 | 35.7239 | 1 | Indicative rail post; Indicative stair rail
THK | AW-THK-C | PILE | 41 | 42.3161 | 11.518 | 0 | 0 | -3.8 | P01 dia600 - display stub; P02 dia600 - display stub; P03 dia600 - display stub; P04 dia600 - display stub; P05 dia600 - display stub; P06 dia600 - display stub
THK | AW-THK-C | RC_BASE | 4 | 307.6169 | 508.7786 | 69.0687 | 0 | -1.17 | 600mm raft with sloping floor and integral hopper; Bridge foundation tab; Bridge foundation tab -; Stair foundation slab
THK | AW-THK-C | RC_BRIDGE | 104 | 5.3303 | 1.29 | 171.0635 | 0 | 5.025 | B1 diagonal -0.75; B1 diagonal 0.75; B3 chord y-0.75 z5; B3 chord y-0.75 z7; B3 chord y0.75 z5; B3 chord y0.75 z7
THK | AW-THK-C | RC_COLBEAM | 6 | 6.876 | 4.96 | 57.5201 | 0 | 0.5 | C2 -1 -0; C2 -1 0; C2 1 -0; C2 1 0; Ground beam 14; Ground beam 15
THK | AW-THK-C | RC_MISC | 1 | 36.6276 | 91.5689 | 155.2776 | 0 | 3.1 | Cantilever channel invert - 400mm
THK | AW-THK-C | RC_SLAB | 4 | 1.65 | 7.25 | 12.93 | 0 | 2.975 | Bridge bearing head; Bridge bearing head -; Intermediate landing +3; Upper landing +5
THK | AW-THK-C | RC_WALL | 2 | 204.8584 | 77.2696 | 764.9436 | 0 | 0.5 | 600mm circular tank wall - clear diameter 23m; Channel outer wall - 400mm
THK | AW-THK-C | STAIRS | 8 | 5.6984 | 8.7 | 0 | 0 | 0.5 | Stair C1 14.1 -1; Stair C1 14.1 0; Stair C1 14.1 5; Stair C1 15.9 -1; Stair C1 15.9 0; Stair C1 15.9 5
THK | AW-THK-D | BLINDING | 1 | 98.1572 | 486.8696 | 0 | 0 | -1.37 | 150mm blinding and 50mm screed envelope
THK | AW-THK-D | GRATING | 1 | 0.21222 | 35.3699 | 0 | 0 | 5.175 | 6mm chequer plate bridge deck
THK | AW-THK-D | HANDRAIL | 28 | 0.11689 | 0.056707 | 0 | 35.7239 | 1 | Indicative rail post; Indicative stair rail
THK | AW-THK-D | PILE | 41 | 42.3162 | 11.518 | 0 | 0 | -3.8 | P01 dia600 - display stub; P02 dia600 - display stub; P03 dia600 - display stub; P04 dia600 - display stub; P05 dia600 - display stub; P06 dia600 - display stub
THK | AW-THK-D | RC_BASE | 4 | 307.617 | 508.7788 | 69.0686 | 0 | -1.17 | 600mm raft with sloping floor and integral hopper; Bridge foundation tab; Bridge foundation tab -; Stair foundation slab
THK | AW-THK-D | RC_BRIDGE | 104 | 5.3303 | 1.29 | 171.0632 | 0 | 5.025 | B1 diagonal -0.75; B1 diagonal 0.75; B3 chord y-0.75 z5; B3 chord y-0.75 z7; B3 chord y0.75 z5; B3 chord y0.75 z7
THK | AW-THK-D | RC_COLBEAM | 6 | 6.8761 | 4.96 | 57.5203 | 0 | 0.5 | C2 -1 -0; C2 -1 0; C2 1 -0; C2 1 0; Ground beam 14; Ground beam 15
THK | AW-THK-D | RC_MISC | 1 | 36.6276 | 91.569 | 155.2777 | 0 | 3.1 | Cantilever channel invert - 400mm
THK | AW-THK-D | RC_SLAB | 4 | 1.65 | 7.25 | 12.93 | 0 | 2.975 | Bridge bearing head; Bridge bearing head -; Intermediate landing +3; Upper landing +5
THK | AW-THK-D | RC_WALL | 2 | 204.8584 | 77.2696 | 764.9436 | 0 | 0.5 | 600mm circular tank wall - clear diameter 23m; Channel outer wall - 400mm
THK | AW-THK-D | STAIRS | 8 | 5.6984 | 8.7 | 0 | 0 | 0.5 | Stair C1 14.1 -1; Stair C1 14.1 0; Stair C1 14.1 5; Stair C1 15.9 -1; Stair C1 15.9 0; Stair C1 15.9 5
DIG | AW-DIG-01 | EXCL | 1 | 10.5843 | 529.2024 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-01 | HANDRAIL | 112 | 0.62036 | 7.3875 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-01 | RC_BASE | 3 | 1246.9151 | 1325.2104 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-01 | RC_MISC | 2 | 4.4297 | 1.2 | 33.9608 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-01 | RC_SLAB | 2 | 151.0669 | 713.5069 | 856.6104 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-01 | RC_WALL | 3 | 1205.7152 | 60.9159 | 3469.0334 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-01 | STAIRS | 1 | 1.6078 | 12.7698 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
DIG | AW-DIG-02 | EXCL | 1 | 10.5843 | 529.202 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-02 | HANDRAIL | 112 | 0.62038 | 7.3878 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-02 | RC_BASE | 3 | 1246.9149 | 1325.2074 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-02 | RC_MISC | 2 | 4.4296 | 1.2 | 33.9606 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-02 | RC_SLAB | 2 | 151.0669 | 713.5048 | 856.6102 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-02 | RC_WALL | 3 | 1205.7173 | 60.9163 | 3469.0336 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-02 | STAIRS | 1 | 1.6079 | 12.7698 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
DIG | AW-DIG-03 | EXCL | 1 | 10.5843 | 529.2025 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-03 | HANDRAIL | 112 | 0.62039 | 7.3875 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-03 | RC_BASE | 3 | 1246.9151 | 1325.2046 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-03 | RC_MISC | 2 | 4.4297 | 1.2001 | 33.9605 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-03 | RC_SLAB | 2 | 151.0669 | 713.5038 | 856.6112 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-03 | RC_WALL | 3 | 1205.714 | 60.916 | 3469.0335 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-03 | STAIRS | 1 | 1.6078 | 12.7697 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
DIG | AW-DIG-04 | EXCL | 1 | 10.5843 | 529.2021 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-04 | HANDRAIL | 112 | 0.6204 | 7.3876 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-04 | RC_BASE | 3 | 1246.9149 | 1325.2092 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-04 | RC_MISC | 2 | 4.4296 | 1.2 | 33.9605 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-04 | RC_SLAB | 2 | 151.067 | 713.5042 | 856.6113 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-04 | RC_WALL | 3 | 1205.7182 | 60.9161 | 3469.0333 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-04 | STAIRS | 1 | 1.6079 | 12.7698 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
DIG | AW-DIG-05 | EXCL | 1 | 10.5843 | 529.2008 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-05 | HANDRAIL | 112 | 0.62038 | 7.3878 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-05 | RC_BASE | 3 | 1246.9148 | 1325.2078 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-05 | RC_MISC | 2 | 4.4296 | 1.2 | 33.9604 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-05 | RC_SLAB | 2 | 151.067 | 713.5029 | 856.61 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-05 | RC_WALL | 3 | 1205.7182 | 60.9161 | 3469.0334 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-05 | STAIRS | 1 | 1.6079 | 12.7698 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
DIG | AW-DIG-06 | EXCL | 1 | 10.5843 | 529.2025 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-06 | HANDRAIL | 112 | 0.62038 | 7.3875 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-06 | RC_BASE | 3 | 1246.9149 | 1325.2081 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-06 | RC_MISC | 2 | 4.4296 | 1.2 | 33.9606 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-06 | RC_SLAB | 2 | 151.067 | 713.5046 | 856.6094 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-06 | RC_WALL | 3 | 1205.7172 | 60.9163 | 3469.0332 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-06 | STAIRS | 1 | 1.6079 | 12.7698 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
DIG | AW-DIG-07 | EXCL | 1 | 10.5843 | 529.203 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-07 | HANDRAIL | 112 | 0.6204 | 7.3877 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-07 | RC_BASE | 3 | 1246.9149 | 1325.2082 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-07 | RC_MISC | 2 | 4.4297 | 1.2 | 33.9608 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-07 | RC_SLAB | 2 | 151.067 | 713.5045 | 856.61 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-07 | RC_WALL | 3 | 1205.7195 | 60.9164 | 3469.0333 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-07 | STAIRS | 1 | 1.6079 | 12.7698 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
DIG | AW-DIG-08 | EXCL | 1 | 10.5843 | 529.2031 | 0 | 0 | 20.68 | Updated hydraulic WL +20.70 reference
DIG | AW-DIG-08 | HANDRAIL | 112 | 0.62038 | 7.3878 | 0 | 105.9579 | 22.1995 | Perimeter rail at 22; Perimeter rail at 23; Perimeter rail post; Roof stair rail -0.7 0; Roof stair rail -0.7 1; Roof stair rail 0.7 0
DIG | AW-DIG-08 | RC_BASE | 3 | 1246.9148 | 1325.2093 | 218.6381 | 0 | -1.7914 | Foundation below sloped structural base; Sloping base with central flat and perimeter shoulder; Valve chamber base
DIG | AW-DIG-08 | RC_MISC | 2 | 4.4296 | 1.2 | 33.9604 | 0 | -1.4914 | Valve chamber side A; Valve chamber side B
DIG | AW-DIG-08 | RC_SLAB | 2 | 151.067 | 713.5049 | 856.61 | 0 | 21.6 | Annular deck overhang; Conical roof and 400 mm central neck opening
DIG | AW-DIG-08 | RC_WALL | 3 | 1205.7177 | 60.9162 | 3469.0333 | 0 | -1.4914 | Cylindrical wall 700 mm; Valve chamber inner wall; Valve chamber outer wall
DIG | AW-DIG-08 | STAIRS | 1 | 1.6079 | 12.7698 | 0 | 0 | 22.1995 | Roof stair 1.20 m clear
GHT | AW-GHT-01 | RC_PLINTH | 1 | 226.189 | 452.3777 | 37.6989 | 0 | -1.5 | Concrete plinth - diameter 24m - provisional 500mm
GHT | AW-GHT-02 | RC_PLINTH | 1 | 226.189 | 452.3784 | 37.6989 | 0 | -1.5 | Concrete plinth - diameter 24m - provisional 500mm
GHT | AW-GHT-03 | RC_PLINTH | 1 | 226.189 | 452.3779 | 37.6989 | 0 | -1.5 | Concrete plinth - diameter 24m - provisional 500mm
GHT | AW-GHT-04 | RC_PLINTH | 1 | 226.189 | 452.378 | 37.6989 | 0 | -1.5 | Concrete plinth - diameter 24m - provisional 500mm
GHB | AW-GHB | RC_BASE | 1 | 17.784 | 59.28 | 9.66 | 0 | -1.5 | Floor slab 300 mm
GHB | AW-GHB | RC_PLINTH | 10 | 1.44 | 4.8 | 8.4 | 0 | -1.2 | North equipment plinth; South equipment plinth
GHB | AW-GHB | RC_SLAB | 1 | 13.52 | 67.6001 | 74.3602 | 0 | 5.8 | Roof slab 200 mm - longitudinal extent provisional
GHB | AW-GHB | RC_WALL | 7 | 60.5261 | 11.5441 | 435.3483 | 0 | -1.2 | Entrance north jamb - head unresolved; Entrance south jamb - head unresolved; North side parapet 150 mm; North wall 300 mm; South side parapet 150 mm; South wall 300 mm
DSB | AW-DSB-01 | RC_BASE | 1 | 256.4698 | 512.9404 | 47.5 | 0 | -2 | Floor slab 500 mm
DSB | AW-DSB-01 | RC_PLINTH | 16 | 26.8321 | 89.44 | 40.0801 | 0 | -1.5 | Layout plinth
DSB | AW-DSB-01 | RC_SLAB | 1 | 174.42 | 581.3989 | 611.5799 | 0 | 6.5 | Roof slab 300 mm
DSB | AW-DSB-01 | RC_WALL | 12 | 255.0328 | 50.5937 | 1772.8701 | 0 | -1.5 | East parapet 200 mm; Front parapet 200 mm; Hall partition wall 300 mm; Main hall end wall 300 mm; Main left front wall; Main right front wall
DSB | AW-DSB-02 | RC_BASE | 1 | 256.4701 | 512.9402 | 47.5 | 0 | -2 | Floor slab 500 mm
DSB | AW-DSB-02 | RC_PLINTH | 16 | 26.832 | 89.4404 | 40.0801 | 0 | -1.5 | Layout plinth
DSB | AW-DSB-02 | RC_SLAB | 1 | 174.4202 | 581.3999 | 611.5802 | 0 | 6.5 | Roof slab 300 mm
DSB | AW-DSB-02 | RC_WALL | 12 | 255.0314 | 50.59 | 1772.8702 | 0 | -1.5 | East parapet 200 mm; Front parapet 200 mm; Hall partition wall 300 mm; Main hall end wall 300 mm; Main left front wall; Main right front wall
GPS | AW-GPS | EXCL | 1 | 0.18 | 9 | 0 | 0 | -2.02 | Water reference at tender WL -2
GPS | AW-GPS | RC_BASE | 1 | 6.912 | 23.04 | 6 | 0 | -3.8 | Base slab 300mm with west toe
GPS | AW-GPS | RC_MISC | 1 | 2.412 | 24.1199 | 2.06 | 0 | -3.9 | Lower layer 100mm
GPS | AW-GPS | RC_SLAB | 5 | 1.98 | 6.6001 | 9.12 | 0 | -1.5 | East cover seat; Front cover seat; Rear cover seat; Removable cover envelope 2.00 x 2.80m; West cover seat
GPS | AW-GPS | RC_WALL | 5 | 14.6256 | 6.3835 | 104.422 | 0 | -3.5 | East wall 300mm; Front wall 300mm; Partition 300mm; Rear wall 300mm; West inlet wall 300mm
SCPS | AW-SCPS | EXCL | 1 | 0.18 | 9 | 0 | 0 | -2.02 | Water reference at tender WL -2
SCPS | AW-SCPS | RC_BASE | 2 | 6.912 | 23.0402 | 8.16 | 0 | -5.3 | Covered chamber base slab300mm; Wet base slab300mm with west toe
SCPS | AW-SCPS | RC_MISC | 1 | 1.49 | 14.9001 | 1.5478 | 0 | -5.4 | Wet lower layer100mm
SCPS | AW-SCPS | RC_SLAB | 6 | 2.952 | 16.3199 | 10.38 | 0 | -3.9 | Covered chamber lower layer100mm; East cover seat; Front cover seat; Rear cover seat; Removable cover envelope 2.00 x 2.80m; West cover seat
SCPS | AW-SCPS | RC_WALL | 7 | 20.5656 | 6.3835 | 150.3822 | 0 | -5 | Deep partition300mm; East wall300mm; Front covered chamber wall300mm; Front wet wall300mm; Rear covered chamber wall300mm; Rear wet wall300mm
WPD | AW-WPD | BLINDING | 1 | 383.5399 | 1917.7002 | 0 | 0 | 0.7 | Unspecified lower continuous layer
WPD | AW-WPD | EXCL | 1 | 0.49652 | 49.6518 | 0 | 0 | 3.99 | WL +4.00 hydraulic reference
WPD | AW-WPD | RC_BASE | 1 | 558.5522 | 1861.8398 | 55.5 | 0 | 0.9 | Main and annex floor envelope
WPD | AW-WPD | RC_MISC | 1 | 17.1871 | 57.2899 | 71.2465 | 0 | 0.9 | Tank bottom envelope
WPD | AW-WPD | RC_PLINTH | 60 | 115.9559 | 386.5197 | 165.9599 | 0 | 1.2 | Dewatering plinth; Narrow support strip; PPU plinth
WPD | AW-WPD | RC_SLAB | 1 | 387.2957 | 1936.4814 | 1974.1214 | 0 | 8.6 | Provisional roof slab200mm
WPD | AW-WPD | RC_WALL | 21 | 460.1032 | 92.9587 | 3229.3137 | 0 | 1.2 | Annex east wall segment; Annex north wall; Annex small room partition; Annex south loading wall segment; East parapet; Main annex partition
THP | AW-THP | RC_PLINTH | 1 | 616 | 1232.0005 | 70.8 | 0 | 1 | THP concrete platform - mixed provisional
FDW | AW-FDW | ARCH | 2 | 12.6867 | 2.8833 | 0 | 0 | 2.3 | Annex front door head envelope; Main door head envelope
FDW | AW-FDW | RC_BASE | 2 | 387.7554 | 1560.7389 | 58.7778 | 0 | -1.2 | Lower layer reference envelope; Stepped floor envelope
FDW | AW-FDW | RC_PLINTH | 24 | 47.094 | 156.9801 | 67.1401 | 0 | -0.7 | Raised civil pad or strip
FDW | AW-FDW | RC_SLAB | 1 | 161.4337 | 807.1671 | 831.0898 | 0 | 6.7 | Stepped roof civil envelope
FDW | AW-FDW | RC_WALL | 18 | 282.4441 | 54.8137 | 1997.0054 | 0 | -0.7 | Annex east lower wall; Annex front access left jamb; Annex front access right jamb; Annex return parapet; Annex room partition; Annex side access lower jamb
CHP | AW-CHP | RC_BASE | 1 | 400.1441 | 1000.3599 | 50.96 | 0 | -1.9 | Floor civil envelope
CHP | AW-CHP | RC_PLINTH | 5 | 40.5 | 134.9999 | 36 | 0 | -1.5 | Raised civil pad
CHP | AW-CHP | RC_SLAB | 1 | 210.3918 | 1051.9595 | 1078.0794 | 0 | 8.5 | Roof envelope
CHP | AW-CHP | RC_WALL | 9 | 373.3501 | 55.8595 | 2584.5999 | 0 | -1.5 | East parapet; East wall; North access wall; North parapet; South parapet; South wall
CHS | AW-CHS | RC_BASE | 5 | 63.2191 | 210.7299 | 52.53 | 0 | -1.6 | Floor slab zone; West perimeter floor strip
CHS | AW-CHS | RC_MISC | 11 | 26.412 | 75.4994 | 159.72 | 0 | -2.1 | Channel 3.35 east closure; Channel 3.35 side; Channel 5.05 east closure; Channel 5.05 side; Longitudinal channel 3.35 bottom; Longitudinal channel 5.05 bottom
CHS | AW-CHS | RC_PLINTH | 2 | 16.56 | 110.4001 | 15.24 | 0 | -1.3 | Raised storage strip
CHS | AW-CHS | RC_SLAB | 9 | 45.605 | 323.0348 | 409.103 | 0 | 3.7 | Longitudinal roof downstand; Roof slab nominal120mm; Transverse roof downstand
CHS | AW-CHS | RC_WALL | 8 | 80.0633 | 28.0868 | 882.9606 | 0 | -1.3 | East loading wall two openings; East parapet; North parapet; North wall with openings; South parapet; South wall with openings
ABPH | AW-ABPH | RC_BASE | 4 | 45.202 | 181.3901 | 42.13 | 0 | 0.2 | Floor zone; Unspecified lower strip
ABPH | AW-ABPH | RC_MISC | 6 | 10.575 | 63.9 | 191.075 | 0 | -0.3 | Trench bottom lining; Trench shell bottom; Trench shell side; Trench side lining
ABPH | AW-ABPH | RC_SLAB | 2 | 30.0134 | 169.5875 | 182.2476 | 0 | 0.65 | Removable trench cover envelope; Roof envelope
ABPH | AW-ABPH | RC_WALL | 9 | 73.8276 | 21.9204 | 534.2839 | 0 | 0.7 | East end wall; East parapet; Front parapet; Front wall; Rear parapet; Rear wall

## Structures
Structures - footprint, excavation, backfill and piles
Footprint = plan convex hull of elements that go below NG. Excavation from NG to the lowest element with working space and side slope (volume of an offset prism). Backfill = excavation - footprint x depth. Piles: modelled count where the model has piles, otherwise an allowance.
Bill | Asset | Structure | Model stage (manifest 19 Oct 2026) | Footprint below NG (m2) | Footprint perimeter (m) | Lowest level (m) | Depth below NG (m) | Excavation (m3) | Backfill (m3) | Base top area (m2) | Piles in model (no.) | Pile basis | Piles for BOQ (no.)
GRT | AW-GRT | Grit removal and fine screens | Civil Guide Rev01 coordination reconstruction | 35.6 | 24.2 | -5.7 | 5 | 1180.792 | 1002.792 | 647.3 | 0 | Allowance: footprint x PILE_DENS | 65
PST | AW-PST | Primary sedimentation package | Eight new basins CGD Rev01 | 6050.3 | 312.8 | -7.6 | 6.9 | 56094.7609 | 14347.6909 | 6454.4 | 0 | Allowance: footprint x PILE_DENS | 646
IPS | AW-IPS | Intermediate pumping station | CGD Rev01 civil envelope | 842.5 | 116.1 | -7.6 | 6.9 | 11780.0457 | 5966.7957 | 801.5 | 0 | Allowance: footprint x PILE_DENS | 85
IPS | AW-IPS-SHARED | Shared IPS / RAS motor hall and distribution channel | CGD Rev01 envelope; once only | 0 | 0 | 3.5 | 0 | 0 | 0 | 321.6 | 0 | Allowance: footprint x PILE_DENS | 33
AER | AW-AER | Aeration tank complex | Structural reconstruction | 34994.8 | 774.3 | -3.1 | 2.4 | 89258.0712 | 5270.5512 | 33611.3 | 3672 | Model (display stubs) | 3672
SDC | AW-SDC-A | Secondary distribution chamber A | CGD Rev02 envelope | 96.8 | 34.9 | -5.7 | 5 | 1740.917 | 1256.917 | 230 | 0 | Allowance: footprint x PILE_DENS | 23
SDC | AW-SDC-B | Secondary distribution chamber B | CGD Rev02 envelope | 96.8 | 34.9 | -5.7 | 5 | 1740.917 | 1256.917 | 230 | 0 | Allowance: footprint x PILE_DENS | 23
SDC | AW-SDC-C | Secondary distribution chamber C | CGD Rev02 envelope | 96.8 | 34.9 | -5.7 | 5 | 1740.917 | 1256.917 | 230 | 0 | Allowance: footprint x PILE_DENS | 23
FST | AW-FST-A | Final sedimentation tank A | Typical structural instance | 2550.4 | 179 | -4.5 | 3.8 | 12519.5641 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-B | Final sedimentation tank B | Typical structural instance | 2550.2 | 179 | -4.5 | 3.8 | 12518.8041 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-C | Final sedimentation tank C | Typical structural instance | 2550.3 | 179 | -4.5 | 3.8 | 12519.1841 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-D | Final sedimentation tank D | Typical structural instance | 2550.3 | 179 | -4.5 | 3.8 | 12519.1841 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-E | Final sedimentation tank E | Typical structural instance | 2550.2 | 179 | -4.5 | 3.8 | 12518.8041 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-F | Final sedimentation tank F | Typical structural instance | 2550.3 | 179 | -4.5 | 3.8 | 12519.1841 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-G | Final sedimentation tank G | Typical structural instance | 2550.3 | 179 | -4.5 | 3.8 | 12519.1841 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-H | Final sedimentation tank H | Typical structural instance | 2550.3 | 179 | -4.5 | 3.8 | 12519.1841 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-I | Final sedimentation tank I | Typical structural instance | 2550.4 | 179 | -4.5 | 3.8 | 12519.5641 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-J | Final sedimentation tank J | Typical structural instance | 2550.2 | 179 | -4.5 | 3.8 | 12518.8041 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-K | Final sedimentation tank K | Typical structural instance | 2550.3 | 179 | -4.5 | 3.8 | 12519.1841 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
FST | AW-FST-L | Final sedimentation tank L | Typical structural instance | 2550.3 | 179 | -4.5 | 3.8 | 12519.1841 | 2828.0441 | 2668.1 | 213 | Model (display stubs; FST stubs are placeholders) | 213
RAS | AW-RASWAS | RAS/WAS pumping station | CGD Rev01 civil envelope | 163.1 | 59.3 | -9 | 8.3 | 6607.7558 | 5254.0258 | 525.8 | 0 | Allowance: footprint x PILE_DENS | 53
CCT | AW-CCT | Chlorine contact tank | Civil Guide Rev01 coordination reconstruction | 3811.7 | 263.9 | -6.6 | 5.9 | 31602.2958 | 9113.2658 | 6762.2 | 0 | Allowance: footprint x PILE_DENS | 677
FIRE | AW-FIRE | Fire / services / cooling | Civil Guide Rev00 coordination reconstruction | 689.1 | 103.7 | -6.5 | 5.8 | 7851.0588 | 3854.2788 | 736.3 | 0 | Allowance: footprint x PILE_DENS | 74
BLOW | AW-BLOW | Air blower building | Civil Guide Rev01 coordination reconstruction | 0 | 0 | -0.05 | 0 | 0 | 0 | 413.4 | 0 | Allowance: footprint x PILE_DENS | 42
THK | AW-THK-A | Primary sludge thickener A | Structural template available | 490.1 | 78.5 | -1.37 | 0.67 | 412.3199 | 83.9529 | 508.8 | 41 | Model (display stubs) | 41
THK | AW-THK-B | Primary sludge thickener B | Structural template available | 490.1 | 78.5 | -1.37 | 0.67 | 412.3199 | 83.9529 | 508.8 | 41 | Model (display stubs) | 41
THK | AW-THK-C | Primary sludge thickener C | Structural template available | 490.1 | 78.5 | -1.37 | 0.67 | 412.3199 | 83.9529 | 508.8 | 41 | Model (display stubs) | 41
THK | AW-THK-D | Primary sludge thickener D | Structural template available | 490.1 | 78.5 | -1.37 | 0.67 | 412.3199 | 83.9529 | 508.8 | 41 | Model (display stubs) | 41
DIG | AW-DIG-01 | Digester 01 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
DIG | AW-DIG-02 | Digester 02 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
DIG | AW-DIG-03 | Digester 03 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
DIG | AW-DIG-04 | Digester 04 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
DIG | AW-DIG-05 | Digester 05 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
DIG | AW-DIG-06 | Digester 06 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
DIG | AW-DIG-07 | Digester 07 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
DIG | AW-DIG-08 | Digester 08 — anaerobic | Mixed-source provisional coordination envelope | 671 | 92.3 | -1.79 | 1.09 | 926.3177 | 194.9277 | 1325.2 | 0 | Allowance: footprint x PILE_DENS | 133
GHT | AW-GHT-01 | Gas holder 01 - civil plinth | Tender provisional civil plinth only; equipment unmodelled | 452.4 | 75.4 | -1.5 | 0.8 | 465.1676 | 103.2476 | 452.4 | 0 | Allowance: footprint x PILE_DENS | 46
GHT | AW-GHT-02 | Gas holder 02 - civil plinth | Tender provisional civil plinth only; equipment unmodelled | 452.4 | 75.4 | -1.5 | 0.8 | 465.1676 | 103.2476 | 452.4 | 0 | Allowance: footprint x PILE_DENS | 46
GHT | AW-GHT-03 | Gas holder 03 - civil plinth | Tender provisional civil plinth only; equipment unmodelled | 452.4 | 75.4 | -1.5 | 0.8 | 465.1676 | 103.2476 | 452.4 | 0 | Allowance: footprint x PILE_DENS | 46
GHT | AW-GHT-04 | Gas holder 04 - civil plinth | Tender provisional civil plinth only; equipment unmodelled | 452.4 | 75.4 | -1.5 | 0.8 | 465.1676 | 103.2476 | 452.4 | 0 | Allowance: footprint x PILE_DENS | 46
GHB | AW-GHB | 010 Gas Holder Blower House | Tender provisional civil envelope | 59.3 | 32.2 | -1.5 | 0.8 | 95.3916 | 47.9516 | 64.1 | 0 | Allowance: footprint x PILE_DENS | 7
DSB | AW-DSB-01 | 014 Digested Sludge Building 01 | Mixed-source provisional civil reconstruction | 513.1 | 95 | -2 | 1.3 | 928.1671 | 261.1371 | 602.4 | 0 | Allowance: footprint x PILE_DENS | 61
DSB | AW-DSB-02 | 014 Digested Sludge Building 02 | Mixed-source provisional civil reconstruction | 513 | 95 | -2 | 1.3 | 928.0371 | 261.1371 | 602.4 | 0 | Allowance: footprint x PILE_DENS | 61
GPS | AW-GPS | 015 Grease Pump Station | Tender provisional civil reconstruction | 24.2 | 20.6 | -3.9 | 3.2 | 437.0837 | 359.6437 | 23 | 0 | Allowance: footprint x PILE_DENS | 3
SCPS | AW-SCPS | 016 Scum Pump Station | Tender provisional civil reconstruction | 24.2 | 20.6 | -5.4 | 4.7 | 915.3398 | 801.5998 | 23 | 0 | Allowance: footprint x PILE_DENS | 3
WPD | AW-WPD | 019 WAS Predewatering Building | Tender provisional civil reconstruction | 0 | 0 | 0.7 | 0 | 0 | 0 | 2248.4 | 0 | Allowance: footprint x PILE_DENS | 225
THP | AW-THP | 021 THP System - civil platform | Tender mixed provisional civil envelope | 0 | 0 | 1 | 0 | 0 | 0 | 1232 | 0 | Allowance: footprint x PILE_DENS | 124
FDW | AW-FDW | 024 New Final Dewatering Building | Tender provisional civil reconstruction | 838.2 | 115 | -1.2 | 0.5 | 501.2059 | 82.1059 | 1717.7 | 0 | Allowance: footprint x PILE_DENS | 172
CHP | AW-CHP | 022 CHP Building | Tender provisional civil reconstruction | 1000.5 | 127.4 | -1.9 | 1.2 | 1505.6993 | 305.0993 | 1135.4 | 0 | Allowance: footprint x PILE_DENS | 114
CHS | AW-CHS | 018 New Chlorination Storage Building | Tender provisional civil reconstruction | 261.4 | 72.9 | -2.1 | 1.4 | 595.2829 | 229.3229 | 321.1 | 0 | Allowance: footprint x PILE_DENS | 33
ABPH | AW-ABPH | 020 Air Blowers Power House | Tender provisional civil reconstruction | 0 | 0 | -0.3 | 0 | 0 | 0 | 181.4 | 0 | Allowance: footprint x PILE_DENS | 19
|  | Total |  | 89852.9 |  |  |  | 376654.0587 | 87172.9007 |  | 6392 |  | 10206

## Pipes
Underground pipework - quantities per line
Lengths, sizes and fittings from the v3 package workbook (21 Oct 2026). Excavation, sheet piles, piled slab, piles, backfill, dewatering and flotation from the sequence workbook (22 Oct 2026: GWL -1.50, all pipes on piled slabs). Surround is a formula.
Line | Material | Printed size | Planning OD (m) | 3D length (m) | Packages | Tie-in / connection ends | Elbow 30 | Elbow 45 | Elbow 90 | Elbow (angle not stated) | Flange | Reducer | Tee | Stub end | Excavation shored (m3) | Excavation open cut (m3) | Sheet pile area (m2) | Sheet pile wall (m) | Piled slab concrete (m3) | Pipe-support piles (no.) | Backfill (m3) | Granular surround (m3) | Dewatered length (m) | Dewatering package-days | Pipe length needing anchor straps (m) | Crossings to locate (no. packages)
UG-01 | GRP | DN2500 | 2.586 | 324.2877 | 3 | 2 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 7889.5844 | 0 | 8811.6433 | 648.5518 | 546.2523 | 215 | 5822.9194 | 2588.7649 | 324.2759 | 241 | 0 | 1
UG-02 | GRP | DN2000 | 2.07 | 267.3657 | 5 | 2 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 5798.4474 | 0 | 6300.5053 | 534.7239 | 409.1679 | 194 | 4496.5749 | 1679.203 | 267.3619 | 464 | 0 | 3
UG-03 | GRP | DN2000 | 2.07 | 186.0648 | 5 | 1 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 4033.5588 | 0 | 4509.5383 | 372.1183 | 282.2179 | 138 | 3146.2977 | 1168.5891 | 186.0592 | 341 | 0 | 5
UG-04 | GRP | DN2000 | 2.07 | 22.7036 | 2 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 472.8419 | 0 | 547.7884 | 45.3098 | 33.9048 | 22 | 367.6422 | 142.5911 | 22.6549 | 129 | 0 | 2
UG-05 | GRP | DN2200 | 2.276 | 306.5183 | 5 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2988.4682 | 3231.1135 | 2891.2441 | 413.0349 | 498.5219 | 220 | 4499.2523 | 2129.2218 | 306.5174 | 393 | 0 | 3
UG-06 | GRP | DN2200 | 2.276 | 299.9074 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 4331.4844 | 0 | 4198.7008 | 599.8144 | 487.3202 | 216 | 2651.9096 | 2083.2991 | 299.9072 | 436 | 0 | 3
UG-07 | GRP | DN2000 | 2.07 | 86.7643 | 4 | 1 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 1012.1648 | 558.5957 | 1093.9102 | 128.9319 | 133.072 | 70 | 1146.1724 | 544.9271 | 86.7273 | 268 | 0 | 4
UG-07A | HDPE | OD1600 | 1.655 | 371.3664 | 12 | 4 | 0 | 10 | 5 | 5 | 4 | 2 | 0 | 0 | 1476.1689 | 2835.2946 | 2091.5403 | 334.3751 | 429.0569 | 284 | 3370.4252 | 1854.7149 | 370.9254 | 960 | 0 | 7
UG-12 | GRP | DN2000 | 2.07 | 233.2608 | 8 | 1 | 4 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 3705.2633 | 1252.1155 | 3920.1678 | 345.4168 | 357.1527 | 184 | 3817.4356 | 1465.0054 | 232.7084 | 598 | 0 | 8
UG-12A | HDPE | DN1600 as printed | 1.633 | 346.3713 | 12 | 4 | 0 | 8 | 2 | 2 | 3 | 2 | 0 | 0 | 530.1433 | 3987.1034 | 761.0763 | 152.2153 | 408.9049 | 268 | 3594.0056 | 1706.9789 | 346.3712 | 1210 | 0 | 7
UG-15 | GRP | DN2000 | 2.07 | 167.9981 | 6 | 1 | 0 | 2 | 2 | 0 | 0 | 1 | 0 | 0 | 3141.7809 | 0 | 3359.9523 | 335.9952 | 255.7572 | 132 | 2334.2621 | 1055.1199 | 167.9976 | 196 | 0 | 3
UG-15A | HDPE | OD1600 | 1.655 | 259.219 | 10 | 4 | 0 | 8 | 2 | 7 | 3 | 2 | 0 | 0 | 3220.4107 | 290.7225 | 4261.5826 | 477.4676 | 298.2358 | 204 | 2860.2496 | 1294.6176 | 258.7338 | 737 | 0 | 7
UG-08 | GRP | DN2600 | 2.69 | 283.1403 | 7 | 2 | 0 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 2482.0253 | 3158.3621 | 2399.9203 | 299.0018 | 519.4826 | 206 | 3535.9437 | 2361.3559 | 283.1139 | 640 | 224.1 | 5
UG-09 | GRP | DN2600 | 2.69 | 287.8229 | 8 | 2 | 0 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 2344.6846 | 3529.7409 | 2320.3816 | 275.598 | 528.0015 | 214 | 3735.8866 | 2400.4084 | 287.799 | 667 | 230.6171 | 6
UG-10 | GRP | DN2600 | 2.69 | 205.676 | 5 | 2 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 2670.3871 | 518.3921 | 2630.0482 | 373.9093 | 377.0756 | 150 | 1662.1728 | 1715.3134 | 205.5987 | 302 | 146.4 | 2
UG-11 | GRP | DN2000 | 2.07 | 189.3502 | 6 | 0 | 3 | 9 | 0 | 0 | 0 | 1 | 0 | 0 | 4448.5968 | 0 | 4538.0541 | 378.7005 | 284.0951 | 144 | 3560.998 | 1189.2232 | 189.3502 | 210 | 0 | 4
UG-11A | HDPE | OD1400 | 1.42 | 206.0309 | 7 | 2 | 0 | 2 | 0 | 0 | 1 | 3 | 3 | 0 | 2358.3885 | 0 | 3200.2142 | 412.0618 | 231.8765 | 152 | 1867.345 | 885.6699 | 206.0309 | 551 | 0 | 4
UG-11B | HDPE | OD1400 | 2.07 | 500.7365 | 14 | 4 | 0 | 10 | 2 | 6 | 3 | 2 | 0 | 0 | 6077.9766 | 0 | 7653.197 | 1001.4731 | 591.7205 | 366 | 4683.3326 | 3144.8996 | 500.7365 | 1098 | 0 | 4
UG-13 | GRP | DN2000 | 2.07 | 166.2127 | 5 | 1 | 0 | 4 | 2 | 0 | 1 | 2 | 0 | 0 | 3492.6808 | 0 | 3656.6797 | 332.4254 | 251.7163 | 124 | 2702.2595 | 1043.9068 | 166.2127 | 304 | 0 | 5
UG-13A | HDPE | OD1400 | 1.4 | 257.9715 | 16 | 7 | 0 | 3 | 0 | 18 | 2 | 2 | 3 | 0 | 3388.8037 | 0 | 4751.0262 | 515.8212 | 270.5307 | 177 | 2868.1476 | 1093.9591 | 257.9106 | 1430 | 0 | 6
UG-13B | HDPE | OD1400 | 2.07 | 294.4134 | 12 | 4 | 0 | 0 | 0 | 20 | 0 | 1 | 3 | 0 | 3741.7125 | 0 | 5321.8037 | 588.7958 | 300.3586 | 174 | 3184.8754 | 1849.0775 | 294.3979 | 767 | 0 | 7
UG-14E | HDPE | OD1600 | 1.6 | 38.6715 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1001.0676 | 0 | 0 | 44.7265 | 28 | 887.1658 | 186.7595 | 37.5876 | 178 | 0 | 0
UG-14F | HDPE | OD1600 | 1.6 | 39.1758 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 333.0858 | 84.5006 | 392.525 | 56.075 | 45.1143 | 28 | 302.6969 | 189.195 | 38.0885 | 169 | 0 | 0
UG-14G | HDPE | OD1600 | 1.6 | 39.5527 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 988.5207 | 0 | 0 | 45.0884 | 28 | 873.6972 | 191.0149 | 38.2988 | 237 | 0 | 1
UG-14H | HDPE | OD1600 | 1.6 | 39.4341 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 988.3716 | 0 | 0 | 45.0547 | 28 | 873.634 | 190.4422 | 38.1766 | 246 | 0 | 1
UG-16A | HDPE | OD1600 | 1.6 | 38.9986 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 329.9764 | 64.9254 | 388.8855 | 55.5551 | 45.0292 | 28 | 280.2289 | 188.339 | 37.7775 | 185 | 0 | 0
UG-16B | HDPE | OD1600 | 1.6 | 39.3936 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 332.6876 | 67.2763 | 392.056 | 56.008 | 45.0351 | 28 | 285.2761 | 190.2467 | 38.1234 | 155 | 0 | 0
UG-16C | HDPE | OD1600 | 1.6 | 39.5956 | 1 | 2 | 0 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1012.689 | 0 | 0 | 46.0071 | 28 | 895.5259 | 191.2222 | 38.3838 | 198 | 0 | 0
UG-16D | HDPE | OD1600 | 1.6 | 37.5574 | 1 | 2 | 0 | 5 | 0 | 0 | 2 | 0 | 0 | 0 | 312.4349 | 64.4099 | 368.2018 | 52.6003 | 42.8052 | 28 | 267.8356 | 181.379 | 36.3001 | 202 | 0 | 1
UG-27I | HDPE | OD1600 | 1.6 | 38.8478 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 9.2607 | 965.6476 | 11.7596 | 1.6799 | 44.6945 | 28 | 861.0883 | 187.6109 | 37.5872 | 244 | 0 | 0
UG-27J | HDPE | OD1600 | 1.6 | 39.3273 | 2 | 4 | 0 | 5 | 0 | 0 | 2 | 0 | 0 | 0 | 1.4277 | 995.266 | 1.7002 | 0.24288 | 45.0269 | 32 | 882.027 | 189.9266 | 38.0646 | 440 | 0 | 1
UG-27K | HDPE | OD1600 | 1.6 | 38.92 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 329.2831 | 61.6462 | 388.1411 | 55.4487 | 45.0315 | 28 | 276.2506 | 187.9595 | 37.7244 | 228 | 0 | 0
UG-27L | HDPE | OD1600 | 1.6 | 39.3721 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 998.2598 | 0 | 0 | 45.0005 | 28 | 883.6604 | 190.1429 | 38.1115 | 218 | 0 | 0
UG-17 | GRP | DN2200 | 2.276 | 368.0757 | 5 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5321.795 | 686.5076 | 5569.1754 | 696.1469 | 599.0476 | 262 | 3939.1572 | 2556.8288 | 368.0735 | 654 | 0 | 5
UG-18 | GRP | DN2200 | 2.276 | 375.0633 | 2 | 1 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5579.2448 | 358.2952 | 5832.6688 | 729.0836 | 611.8728 | 256 | 3817.3325 | 2605.3677 | 375.0609 | 186 | 0 | 2
UG-19 | GRP | DN1800 | 1.863 | 115.2442 | 3 | 1 | 10 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1642.9328 | 0 | 1838.8621 | 230.4843 | 164.7301 | 86 | 1165.4116 | 648.7943 | 115.2421 | 314 | 0 | 3
UG-20 | GRP | DN1800 | 1.863 | 109.7259 | 2 | 1 | 6 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1570.0578 | 0 | 1755.6054 | 219.4507 | 156.834 | 78 | 1115.4642 | 617.7273 | 109.7253 | 191 | 0 | 2
UG-21 | GRP | DN2200 | 2.276 | 12.2026 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.0006 | 0 | 292.8622 | 24.4052 | 19.9903 | 12 | 219.3467 | 84.765 | 12.2026 | 24 | 0 | 1
UG-22 | GRP | DN2200 | 2.276 | 12.2104 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.1853 | 0 | 293.0494 | 24.4208 | 20.003 | 12 | 219.4869 | 84.8192 | 12.2104 | 24 | 0 | 1
UG-23 | HDPE | OD600 | 0.63 | 295.1333 | 10 | 2 | 0 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 1079.5976 | 1183.2393 | 1769.8893 | 209.0891 | 239.6801 | 113 | 1931.4916 | 629.8663 | 294.0926 | 489 | 0 | 8
UG-24 | GRP | DN2000 | 2.07 | 126.8311 | 2 | 1 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 656.4329 | 1077.8977 | 700 | 140 | 189.915 | 92 | 1145.2227 | 796.5688 | 126.8311 | 181 | 0 | 2
UG-25 | GRP | DN2400 | 2.484 | 495.2172 | 1 | 0 | 0 | 8 | 3 | 0 | 0 | 0 | 0 | 0 | 8609.0665 | 0 | 8913.9093 | 990.4344 | 862.2591 | 334 | 5350.1097 | 3782.1466 | 495.2172 | 140 | 0 | 1
UG-26 | GRP | DN2400 | 2.484 | 495.7154 | 1 | 0 | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 8189.5843 | 0 | 7931.4332 | 991.4292 | 863.4343 | 334 | 4924.6483 | 3785.9508 | 495.7146 | 110 | 0 | 1
UG-28 | HDPE | OD500 | 0.5 | 13.5454 | 2 | 4 | 0 | 4 | 1 | 0 | 1 | 0 | 0 | 0 | 152.4565 | 0 | 248.9085 | 24.8909 | 9.3341 | 8 | 140.6787 | 24.4312 | 12.4454 | 26 | 0 | 2
UG-28A | HDPE | OD315 | 0.315 | 17.8374 | 1 | 2 | 0 | 0 | 3 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 24.0054 | 0 | 0 | 0 | 1
Total |  |  |  | 8168.8302 | 201 | 90 | 27 | 219 | 88 | 58 | 43 | 27 | 10 | 2 | 104633.083 | 29959.9607 | 116308.6076 | 13123.1866 | 11770.1362 | 5788 | 97445.5446 | 51302.3561 | 8132.4305 | 16981 | 601.1171 | 129

## Exclusions
Exclusions, gaps and how to improve the estimate
Item | Status
Preliminaries, site establishment, supervision, insurances, contingency | Not included.
Mechanical, electrical, instrumentation and process equipment | Not included. Equipment envelopes in the model are listed as counts only.
Architecture and finishes (doors, windows, cladding, finishes, MEP in buildings) | Not included; building walls are measured as concrete envelopes (material TBC).
Pile lengths | No pile design lengths in the model (display stubs). Piles are counted, not measured in metres.
Piles for structures without pile layouts | Allowance = footprint x PILE_DENS (calibrated on aeration). Replace with pile designs.
Pipe-support piles | Placeholder layout (rows at 3 m, 2 per row for OD >= 1.0 m). Replace with design.
Reinforcement | Ratios per element class (Inputs). Only the aeration raft ratio is evidence-based.
Dewatering and temporary works for structures | Not quantified (no temporary works design); pipe dewatering and sheet piles are included.
Existing structures and boundaries not in the model | Existing PST, bypass / outfall chambers, treated effluent pump station, inlet / outlet boundaries, primary and thickened sludge pump stations, sludge flowmeter chambers: not measured.
Structures modelled from tender / provisional envelopes | Digesters, gas holders, sludge buildings, pump stations, CHP, THP, final dewatering: Confidence D.
Typical structures | FST A-L and thickeners A-D are typical structures placed 12 and 4 times; tank-specific differences not captured.
Work done | Gross quantities; no deduction for work executed (e.g. 2,079 aeration piles recorded done).
Common vertical datum | Not verified (R001); depths and excavation depend on it.
Site raising | Provisional: developed area is the convex hull of the model; levels NG -0.70 / FL +1.00 are single site values.
Roads, drainage, landscaping, fencing, utilities, cable ducts | Not in the model - not included.